## Front Cover
Issue Status: | Tender Issue
Document Ref: | 27618-975700
Date of Issue: | 2022-04-29
Revision: | P01
(see next page for details)
Author: | Robert Francis
Checked By: | Barry Turpin
Approved By: | Simon Ramsden
Copyright  HILSON MORAN PARTNERSHIP LTD – 2019 All rights reserved. This Technical Specification has been produced by Hilson Moran Partnership Ltd. No part of this document may be reproduced in any material form without the written permission of a Director of Hilson Moran Partnership Ltd. Enquiries about copyright should be made to the Technical Director at the Hilson Moran Partnership Ltd offices in London.
TECHNICAL SCHEDULES
FOR THE
ELECTRICAL SERVICES
SCHEDULE OF LUMINAIRES

## Revision History
SCHEDULE REVISION HISTORY
Rev. | Date | Schedule | Details
P01 | 29 April 2022 | ALL | TENDER ISSUE
Gary Dunlop

## E975700
E975700 | Schedule of Luminaires
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Refurbishment
INDEX TO SCHEDULES
E975701 | Luminaires Type A & AE | Open Plan Office
E975702 | Luminaires Type A1 & A1E | Open Plan Office
E975703 | Luminaires Type A2 & A2E | Open Plan Office
E975704 | Luminaires Type A3 & A3E | Open Plan Office
E975705 | Luminaires Type A4 & A4E | Open Plan Office
E975706 | Luminaires Type A5 & A5E | Open Plan Office
E975707 | Luminaires Type A6 & A6E | Open Plan Office
E975708 | Luminaires Type D1 & D1E | Toilets, changing etc
E975709 | Luminaires Type D2 & D2E | Lounge
E975710 | Luminaires Type D3 & D3E | Stair Landing
E975711 | Luminaires Type D4 & D4E | 2nd Floor Boardroom
E975712 | Luminaires Type P1 | Luminaires Type P1
E975713 | Luminaires Type P2 | Luminaires Type P2
E975714 | Luminaires Type W1 | Lift Lobby (Wall)
E975715 | Luminaires Type W2 | Stairs
E975716 | Luminaires Type W3 | Lounge
E975717 | Luminaires Type W4 | tbc
E975718 | Luminaires Type S1 & S1E | Plant / temporary
E975719 | Luminaires Type T1 | Gym
E975720 | Luminaires Type T2 | Gym
E975721 | Luminaire Type Linear LED Tape | 2nd Floor Boardroom
E975722 | Luminaires Type X1/X1E | Banking Hall Refurbished
E975723 | Luminaires Type X2/X2E | Banking Hall Refurbished
E975724 | Luminaires Type E1 | Emergency
E975725 | Luminaires Type E2 | Emergency
E975726 | Luminaires Type E3 | Emergency
E975727 | Luminaires Type E4 | Emergency
E975728 | Luminaires Type E5 | External emergency
E975729 | Exit Signage | Exit Signage
Last Page | Notes | Notes

## E975701
E975701 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | A & AE
LOCATION: | General Open Plan Office
DESCRIPTION | Surface mounted (to underside of cable tray) 1690mm linear LED luminaire with opal diffuser finished in black. Direct only
Manufacturer(s) | LDL Lighting
Model | Millie Surface
Cat. No. | MIL/S/16/OP/3010/4/BLK/DIM and MIL/S/16/OP/3010/4/BLK/DIM/EMP
Lamp | LED
Lamp output | 3013 lumens
Lamp colour | 4000K
CRI | >80
LED Life Expectancy | L80/B10 78,000 hours
IP rating | IP20
Light distribution | Downward
Control gear | DALI dimming
Dimming | Yes
Efficacy | 139 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 22 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 1690mm x 57mm x 75mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975702
E975702 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | A1 & A1E
LOCATION: | General Open Plan Office
DESCRIPTION | Surface mounted (to underside of cable tray) 1130mm linear LED luminaire with opal diffuser finished in black. Direct only
Manufacturer(s) | LDL Lighting
Model | Millie Surface
Cat. No. | MIL/S/11/MP/2500/4/BLK/DIM and MIL/S/16/MP/2500/4/BLK/DIM/EMP
Lamp | LED
Lamp output | 2499 lumens
Lamp colour | 4000K
CRI | >80
LED Life Expectancy | L80/B10 78,000 hours
IP rating | IP20
Light distribution | Downward
Control gear | DALI dimming
Dimming | Yes
Efficacy | 126 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 20 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 1130mm x 57mm x 75mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975703
E975703 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | A2 & A2E
LOCATION: | General Open Plan Office
DESCRIPTION | Surface mounted (to underside of cable tray) 1410mm linear LED luminaire with opal diffuser finished in black. Direct only
Manufacturer(s) | LDL Lighting
Model | Millie Surface
Cat. No. | MIL/S/14/OP/3300/4/BLK/DIM and MIL/S/14/OP/3300/4/BLK/DIM/EMP
Lamp | LED
Lamp output | 3300 lumens
Lamp colour | 4000K
CRI | >80
LED Life Expectancy | L80/B10 78,000 hours
IP rating | IP20
Light distribution | Downward
Control gear | DALI dimming
Dimming | Yes
Efficacy | 139 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 22 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 1410mm x 57mm x 75mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975704
E975704 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | A3 & A3E
LOCATION: | General Open Plan Office
DESCRIPTION | Surface mounted (to underside of cable tray) 1690mm linear LED luminaire with opal diffuser finished in black. Direct only
Manufacturer(s) | LDL Lighting
Model | Millie Surface
Cat. No. | MIL/S/16/OP/3990/4/BLK/DIM and MIL/S/16/OP/3990/4/BLK/DIM/EMP
Lamp | LED
Lamp output | 3993 lumens
Lamp colour | 4000K
CRI | >80
LED Life Expectancy | L80/B10 78,000 hours
IP rating | IP20
Light distribution | Downward
Control gear | DALI dimming
Dimming | Yes
Efficacy | 138 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 29 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 1690mm x 57mm x 75mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975705
E975705 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | A4 & A4E
LOCATION: | General Open Plan Office
DESCRIPTION | Surface mounted (to underside of cable tray) 2250mm linear LED luminaire with opal diffuser finished in black. Direct only
Manufacturer(s) | LDL Lighting
Model | Millie Surface
Cat. No. | MIL/S/22/OP/5000/4/BLK/DIM and MIL/S/22/OP/5000/4/BLK/DIM/EMP
Lamp | LED
Lamp output | 5000 lumens
Lamp colour | 4000K
CRI | >80
LED Life Expectancy | L80/B10 78,000 hours
IP rating | IP20
Light distribution | Downward
Control gear | DALI dimming
Dimming | Yes
Efficacy | 138 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 35 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 2250mm x 57mm x 75mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975706
E975706 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | A5 & A5E
LOCATION: | General Open Plan Office
DESCRIPTION | Surface mounted (to underside of cable tray) 2810mm linear LED luminaire with opal diffuser finished in black. Direct only
Manufacturer(s) | LDL Lighting
Model | Millie Surface
Cat. No. | MIL/S/28/OP/6600/4/BLK/DIM and MIL/S/28/OP/6600/4/BLK/DIM/EMP
Lamp | LED
Lamp output | 6600 lumens
Lamp colour | 4000K
CRI | >80
LED Life Expectancy | L80/B10 78,000 hours
IP rating | IP20
Light distribution | Downward
Control gear | DALI dimming
Dimming | Yes
Efficacy | 138 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 40 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 2810mm x 57mm x 75mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975707
E975707 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | A6 & A6E
LOCATION: | General Open Plan Office
DESCRIPTION | Surface mounted (to underside of cable tray) 3370mm linear LED luminaire with opal diffuser finished in black. Direct only
Manufacturer(s) | LDL Lighting
Model | Millie Surface
Cat. No. | MIL/S/33/OP/7980/4/BLK/DIM and MIL/S/33/OP/7980/4/BLK/DIM/EMP
Lamp | LED
Lamp output | 7980 lumens
Lamp colour | 4000K
CRI | >80
LED Life Expectancy | L80/B10 78,000 hours
IP rating | IP20
Light distribution | Downward
Control gear | DALI dimming
Dimming | Yes
Efficacy | 138 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 45 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 3370mm x 57mm x 75mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975708
E975708 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | D1 & D1E
LOCATION: | Toilets, Showers & Changing Cubicles
DESCRIPTION | Recessed circular downlight, IP44
Manufacturer(s) | Delta Light
Model | Entero RD-S IP Soft 93045
Cat. No. | 28407 9030 B
Lamp | LED
Lamp output | 934 lumens (source); 607 lumens (luminaire)
Lamp colour | 3000K
CRI | >90
LED Life Expectancy | tbc
IP rating | IP44
Light distribution | Downward
Control gear | Standard electronic control gear
Dimming | No
Efficacy | 64 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 10 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 84mm dia. x 108mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975709
E975709 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | D2 & D2E
LOCATION: | Lounge/Reception
DESCRIPTION | Recessed circular downlight
Manufacturer(s) | Delta Light
Model | DIRO SBL L83
Cat. No. | 202 297 83 B
Lamp | LED
Lamp output | 2635 lumens (source); 1443 lumens (luminaire)
Lamp colour | 3000K
CRI | >80
LED Life Expectancy | tbc
IP rating | IP43
Light distribution | Downward
Control gear | DALI dimmable
Dimming | Yes (as required)
Efficacy | 72 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 20W watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 218mm dia. x 63mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975710
E975710 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | D3 & D3E
LOCATION: | Stair Landings
DESCRIPTION | Recessed circular downlight,
Manufacturer(s) | Delta Light
Model | Entero RD-S Soft 93045
Cat. No. | 28407 9030 B
Lamp | LED
Lamp output | 934 lumens (source); 607 lumens (luminaire)
Lamp colour | 3000K
CRI | >90
LED Life Expectancy | tbc
IP rating | IP20
Light distribution | Downward
Control gear | Standard electronic control gear
Dimming | No
Efficacy | 64 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 10 watts
Colour / finish | Black (RAL 9005)
Emergency lighting | Yes (as required)
Dimensions | 84mm dia. x 108mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975711
E975711 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | D4 & D4E
LOCATION: | 2nd Floor Boardroom
DESCRIPTION | Recessed adjustable circular downlight
Manufacturer(s) | LDL Lighting
Model | Felix
Cat. No. | FEL/2004/84
Lamp | LED
Lamp output | 1947 lumens
Lamp colour | 4000K
CRI | 80
LED Life Expectancy | tbc
IP rating | IP20
Light distribution | Downward
Control gear | Standard electronic control gear
Dimming | No
Efficacy | 64 lamp lumens / circuit watt
Luminaire maximum circuit Watts | 17 watts
Colour / finish | White (RAL 9016)
Emergency lighting | Yes (as required)
Dimensions | 150mm dia. x 130mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975712
E975712 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | P1
LOCATION: | Circulation Spaces
DESCRIPTION | Architectural Feature Pendant (details to be confirmed). Electrical Services Installer to allow provisional sum of £300 per luminaire to supply. Install costs to be included as part of ESI tender
Manufacturer(s) | to be confirmed
Model | to be confirmed
Cat. No. | to be confirmed
Lamp | to be confirmed
Lamp output | to be confirmed
Lamp colour | to be confirmed
CRI | to be confirmed
LED Life Expectancy | to be confirmed
IP rating | to be confirmed
Light distribution | to be confirmed
Control gear | to be confirmed
Dimming | to be confirmed
Efficacy | to be confirmed
Luminaire maximum circuit Watts | to be confirmed
Colour / finish | to be confirmed
Emergency lighting | to be confirmed
Dimensions | to be confirmed
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975713
E975713 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | P2
LOCATION: | Office
DESCRIPTION | Architectural Feature Pendant (details to be confirmed). Electrical Services Installer to allow provisional sum of £300 per luminaire to supply. Install costs to be included as part of ESI tender
Manufacturer(s) | to be confirmed
Model | to be confirmed
Cat. No. | to be confirmed
Lamp | to be confirmed
Lamp output | to be confirmed
Lamp colour | to be confirmed
CRI | to be confirmed
LED Life Expectancy | to be confirmed
IP rating | to be confirmed
Light distribution | to be confirmed
Control gear | to be confirmed
Dimming | to be confirmed
Efficacy | to be confirmed
Luminaire maximum circuit Watts | to be confirmed
Colour / finish | to be confirmed
Emergency lighting | to be confirmed
Dimensions | to be confirmed
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975714
E975714 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | W1
LOCATION: | Lift Lobby
DESCRIPTION | Architectural Feature Wall Mounted Luminaire (details to be confirmed). Electrical Services Installer to allow provisional sum of £300 per luminaire to supply. Install costs to be included as part of ESI tender
Manufacturer(s) | to be confirmed
Model | to be confirmed
Cat. No. | to be confirmed
Lamp | to be confirmed
Lamp output | to be confirmed
Lamp colour | to be confirmed
CRI | to be confirmed
LED Life Expectancy | to be confirmed
IP rating | to be confirmed
Light distribution | to be confirmed
Control gear | to be confirmed
Dimming | to be confirmed
Efficacy | to be confirmed
Luminaire maximum circuit Watts | to be confirmed
Colour / finish | to be confirmed
Emergency lighting | to be confirmed
Dimensions | to be confirmed
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975715
E975715 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | W2E
LOCATION: | Staircase
DESCRIPTION | Wall mounted surface LED luminaire with integral 3 hour battery.
Manufacturer(s) | Delta Light
Model | Montur L PC LED
Cat. No. | 232 318 83 B
Lamp | LED
Lamp output | 2300 lumens (source); 1114 lumens (luminaire)
Lamp colour | 3000K
CRI | 80
LED Life Expectancy | tbc
IP rating | IP54
Light distribution | General
Control gear | Standard electronic driver
Dimming | No
Efficacy | 66 lumens/circuit watt
Luminaire maximum circuit Watts | 17W
Colour / finish | Black
Emergency lighting | Yes
Dimensions | 140mm x 140mm x 484mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975716
E975716 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | W3
LOCATION: | Lounge/Reception
DESCRIPTION | Architectural Feature Wall Mounted Luminaire (details to be confirmed). Electrical Services Installer to allow provisional sum of £300 per luminaire to supply. Install costs to be included as part of ESI tender
Manufacturer(s) | to be confirmed
Model | to be confirmed
Cat. No. | to be confirmed
Lamp | to be confirmed
Lamp output | to be confirmed
Lamp colour | to be confirmed
CRI | to be confirmed
LED Life Expectancy | to be confirmed
IP rating | to be confirmed
Light distribution | to be confirmed
Control gear | to be confirmed
Dimming | to be confirmed
Efficacy | to be confirmed
Luminaire maximum circuit Watts | to be confirmed
Colour / finish | to be confirmed
Emergency lighting | to be confirmed
Dimensions | to be confirmed
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975717
E975717 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | W4
LOCATION: | TBC
DESCRIPTION | Architectural Feature Wall Mounted Luminaire (details to be confirmed). Electrical Services Installer to allow provisional sum of £300 per luminaire to supply. Install costs to be included as part of ESI tender
Manufacturer(s) | to be confirmed
Model | to be confirmed
Cat. No. | to be confirmed
Lamp | to be confirmed
Lamp output | to be confirmed
Lamp colour | to be confirmed
CRI | to be confirmed
LED Life Expectancy | to be confirmed
IP rating | to be confirmed
Light distribution | to be confirmed
Control gear | to be confirmed
Dimming | to be confirmed
Efficacy | to be confirmed
Luminaire maximum circuit Watts | to be confirmed
Colour / finish | to be confirmed
Emergency lighting | to be confirmed
Dimensions | to be confirmed
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975718
E975718 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | S1 & S1E
LOCATION: | Plant and general areas
DESCRIPTION | Wall or ceiling surface mounted IP66 non-corrosive industrial LED luminaire
Manufacturer(s) | LDL Lighting
Model | WPZ
Cat. No. | WPZ/5/4510/4 and WPZ/5/4510/4/EMP
Lamp | LED
Lamp output | 4512 lumens
Lamp colour | 4000K
CRI | 80
LED Life Expectancy | L90/B10 100,000 hours
IP rating | IP66 (IK08)
Light distribution | Downward
Control gear | Standard electronic driver
Dimming | No
Efficacy | 149 lumens/circuit watt
Luminaire maximum circuit Watts | 30W
Colour / finish | Grey
Emergency lighting | Yes
Dimensions | 1575mm x 101mm x 84mm
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975719
E975719 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | T1
LOCATION: | Gym
DESCRIPTION | Track mounted linear LED luminaire, within recessed magnetic track
Manufacturer(s) | Delta Light
Model | LED Line OK ADM
Cat. No. | 29311 9305 B
Lamp | LED
Lamp output | 2200 lumens
Lamp colour | 3000K
CRI | 80
LED Life Expectancy | To be confirmed
IP rating | IP20
Light distribution | Downward
Control gear | DALI
Dimming | Yes
Efficacy | To be confirmed
Luminaire maximum circuit Watts | 18.4W
Colour / finish | Black
Emergency lighting | No
Dimensions | 815mm x 66mm x 30mm
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975720
E975720 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | T2
LOCATION: | Gym
DESCRIPTION | Track mounted dynamic LED spotlight luminaire, within recessed magnetic track
Manufacturer(s) | Delta Light
Model | Maxispy Dynamic Focus 930 ADM WD
Cat. No. | 19880 930W B
Lamp | LED
Lamp output | 724 lumens
Lamp colour | 3000K
CRI | 80
LED Life Expectancy | To be confirmed
IP rating | IP20
Light distribution | Downward
Control gear | DALI
Dimming | Yes
Efficacy | To be confirmed
Luminaire maximum circuit Watts | 17W
Colour / finish | Black
Emergency lighting | No
Dimensions | 90mm dia x 165mm
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975721
E975721 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | LED Tape System
LOCATION: | 2nd Floor Boardroom
DESCRIPTION | LED tape around cove within extruded diffuser (details to be confirmed)
Manufacturer(s) | LDL Lighting
Model | LED Tape
Cat. No. | LDT/18/2400/6/DIM
Lamp | LED
Lamp output | 1800 lumens / metre
Lamp colour | 6500K
CRI | 80
LED Life Expectancy | L80/B10 72,000 hours
IP rating | IP00
Light distribution | Downward
Control gear | DALI
Dimming | Yes
Efficacy | 147 lumens/circuit watt
Luminaire maximum circuit Watts | 11.3W / metre
Colour / finish | n/a
Emergency lighting | No
Dimensions | 8mm x length
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975722
E975722 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | X1 & X1E
LOCATION: | Banking Hall
DESCRIPTION | Refurbishment of existing pendant luminaire (subject to intrusive investigation, provisional sum included)
Manufacturer(s) | LDL Lighting
Model | to be confirmed
Cat. No. | to be confirmed
Lamp | to be confirmed
Lamp output | to be confirmed
Lamp colour | to be confirmed
CRI | to be confirmed
LED Life Expectancy | to be confirmed
IP rating | to be confirmed
Light distribution | to be confirmed
Control gear | to be confirmed
Dimming | to be confirmed
Efficacy | to be confirmed
Luminaire maximum circuit Watts | to be confirmed
Colour / finish | to be confirmed
Emergency lighting | to be confirmed
Dimensions | to be confirmed
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975723
E975723 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | X2 & X2E
LOCATION: | Banking Hall
DESCRIPTION | Refurbishment of existing wall mounted uplight luminaire (subject to intrusive investigation, provisional sum included)
Manufacturer(s) | LDL Lighting
Model | to be confirmed
Cat. No. | to be confirmed
Lamp | to be confirmed
Lamp output | to be confirmed
Lamp colour | to be confirmed
CRI | to be confirmed
LED Life Expectancy | to be confirmed
IP rating | to be confirmed
Light distribution | to be confirmed
Control gear | to be confirmed
Dimming | to be confirmed
Efficacy | to be confirmed
Luminaire maximum circuit Watts | to be confirmed
Colour / finish | to be confirmed
Emergency lighting | to be confirmed
Dimensions | to be confirmed
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975724
E975717 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | E1
LOCATION: | Various
DESCRIPTION | Recessed discrete LED non-maintained emergency luminaire with open area optic and integral 3 hour DALI EMP driver & LiFePO4 battery.
Manufacturer(s) | LDL Lighting
Model | LED3/kit
Cat. No. | LED3/KIT/W/OA/EMP
Lamp | LED
Lamp output | 266 lumens
Lamp colour | n/a
CRI | n/a
LED Life Expectancy | n/a
IP rating | IP20
Light distribution | Downward (area optic)
Control gear | DALI emergency
Dimming | No
Efficacy | n/a
Luminaire maximum circuit Watts | 2 watts
Colour / finish | White (RAL 9016)
Emergency lighting | Yes
Dimensions | 50mm diameter x 40mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975725
E975718 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | E2
LOCATION: | Various
DESCRIPTION | Recessed discrete LED non-maintained emergency luminaire with corridor optic and integral 3 hour DALI EMP driver & LiFePO4 battery.
Manufacturer(s) | LDL Lighting
Model | LED3/kit
Cat. No. | LED3/KIT/W/CO/EMP
Lamp | LED
Lamp output | 266 lumens
Lamp colour | n/a
CRI | n/a
LED Life Expectancy | n/a
IP rating | IP20
Light distribution | Downward (corridor optic)
Control gear | DALI emergency
Dimming | No
Efficacy | n/a
Luminaire maximum circuit Watts | 2 watts
Colour / finish | White (RAL 9016)
Emergency lighting | Yes
Dimensions | 50mm diameter x 40mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975726
E975719 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | E3
LOCATION: | Various
DESCRIPTION | Surface mounted LED non-maintained emergency luminaire with open area optic and integral 3 hour DALI EMP driver & LiFePO4 battery.
Manufacturer(s) | LDL Lighting
Model | TR2 Surface
Cat. No. | TR2/SF/3/NM/RE/WHI/DALI/OA
Lamp | LED
Lamp output | 217 lumens
Lamp colour | 6500K
CRI | n/a
LED Life Expectancy | n/a
IP rating | IP20
Light distribution | Downward (open area optic)
Control gear | DALI emergency
Dimming | No
Efficacy | n/a
Luminaire maximum circuit Watts | 3 watts
Colour / finish | White (RAL 9016)
Emergency lighting | Yes
Dimensions | 123mm x 123mm x 33mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975727
E975719 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | E4
LOCATION: | Various
DESCRIPTION | Surface mounted LED non-maintained emergency luminaire with corridor optic and integral 3 hour DALI EMP driver & LiFePO4 battery.
Manufacturer(s) | LDL Lighting
Model | TR2 Surface
Cat. No. | TR2/SF/3/NM/RE/WHI/DALI/CO
Lamp | LED
Lamp output | 217 lumens
Lamp colour | 6500K
CRI | n/a
LED Life Expectancy | n/a
IP rating | IP20
Light distribution | Downward (corridor optic)
Control gear | DALI emergency
Dimming | No
Efficacy | n/a
Luminaire maximum circuit Watts | 3 watts
Colour / finish | White (RAL 9016)
Emergency lighting | Yes
Dimensions | 123mm x 123mm x 33mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975728
E975703 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | E5
LOCATION: | External above final exit doors
DESCRIPTION | Surface mounted IP65 LED non-maintained emergency bulkhead luminaire with integral 3 hour DALI EMP driver & LiFePO4 battery.
Manufacturer(s) | LDL Lighting
Model | LD5S
Cat. No. | LD5S/5W/DA
Lamp | LED
Lamp output | 245 lumens
Lamp colour | 6500K
CRI | n/a
LED Life Expectancy | n/a
IP rating | IP20
Light distribution | Downward (corridor optic)
Control gear | DALI emergency
Dimming | No
Efficacy | n/a
Luminaire maximum circuit Watts | 5.5 watts
Colour / finish | tbc
Emergency lighting | Yes (as required)
Dimensions | 276mm x143mm x 44mm deep
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## E975729
E975729 | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Cat A Refurbishment
LUMINAIRE REF: | EXIT SIGN
LOCATION: | General Open Plan Offices
DESCRIPTION | IP20 maintained/non-maintained emergency exit sign, surface mounted on ceiling, self-test finished in white
Manufacturer(s) | LDL Lighting
Model | Exel LED
Cat. No. | as required to meet the performance requirements
Lamp | LED
Lamp output | as required to meet the performance requirements
Lamp colour | n/a
CRI | n/a
LED Life Expectancy | n/a
IP rating | IP20
Light distribution | n/a
Control gear | DALI self test
Dimming | No
Efficacy | n/a
Luminaire maximum circuit Watts | n/a
Colour / finish | White (RAL 9010)
Emergency lighting | Yes (maintained or non-maintained to suit BCO)
Dimensions | 300mm x 90mm x 210mm high
To be read in conjunction Section E57 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification

## Notes
NOTES | SCHEDULE OF LUMINAIRES
HM PROJECT: | 27618
REVISION: | 01
PROJECT NAME: | 38-42 Mosley Street Grade 2* Listed Building Refurbishment
01 | Luminaires shall be selected in accordance with the specific requirements of the Services Description and Section E57 of the specifcation
02 | The stated Manufacturers are advised as an indication of a possible source of equipment likely to comply with specification requirements and be accepted when submitted. Other Manufacturers offering equipment of similar appearance and equal or better quality and performance and fully compliant with the requirements of the specification may be submitted for consideration. Further manufacturers are lsited within schedule E970004
03 | Any dimensional information shown to be confirmed by the Electrical Services Installer with manufacturer prior to its use in co-ordination or construction
04 | The Electrical Services Installer shall submit all necessary Photometric data with the technical submittal for the luminaires