Odour Risk Assessment

Site:

19-21 George Street,

Manchester

M1 4HE

The following ‘Risk Assessment for Odour’ is derived from criteria outlined by EMAQ+ Guidance on the Control of Odour from Commercial Kitchen Exhaust Systems, which superseded DEFRA 2005.

Odour control must be designed to prevent odour nuisance in a given situation. The following score methodology is suggested for determining odour control requirements using a simple risk assessment approach.

The odour control requirements considered here are consistent with the performance requirements listed in this report.

The assessment will establish the appropriate filtration systems for incorporation into the kitchen extract design.

Table 1:

| Impact Risk | Odour Control Requirement | Significance Score* |
| --- | --- | --- |
| Low to Medium | Low-level odour control | Less than 20 |
| High | High-level odour control | 20 to 35 |
| Very High | Very high-level odour control | More than 35 |

* Based on the sum of contributions from dispersion, the proximity of receptors, size of kitchen and cooking type:

Table 2:

| Criteria | Rating | Score | Details |
| --- | --- | --- | --- |
| Dispersion | Very poor | 20 | Low-level discharge, discharge into courtyard or restriction on the stack. |
|  | Poor | 15 | Not low level but below eaves, or discharge at below 10 m/s |
|  | Moderate | 10 | Discharging 1m above eaves at 10-15 m/s |
|  | Good | 5 | Discharging 1m above ridge at 15 m/s |
| Proximity of receptors | Close | 10 | The closest sensitive receptor less than 20m from kitchen discharge |
|  | Medium | 5 | The closest sensitive receptor between 20 and 100m from kitchen discharge |
|  | Far | 1 | Closest sensitive receptor more than 100m from kitchen discharge |
| Size of Kitchen | Large | 5 | More than 100 covers (several vendors) |
|  | Medium | 3 | Between 30 and 100 covers or medium-sized take away |
|  | Small | 1 | Less than 30 covers or small takeaway |
| Cooking type (odour and Grease loading) | Very high | 10 | Pub (high level of fried food), fried chicken, burgers or fish and chips |
|  | High | 7 | Kebab, Vietnamese, Thai or Indian |
|  | Medium | 4 | Cantonese, Japanese or Chinese |
|  | Low | 1 | Most pubs, Italian, French, pizza or steakhouse |