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Mike Thomas 
SES Electrical Project Manager
Think Park, building Three.
Mosley Road. Trafford Park,
Manchester M17 1FQ
mthomas@ses-ltd.co.uk




Planning Ref: 134288/FO/2022
Project Name: No. 3 Circle Square, Manchester
Condition 23: Lighting scheme


Dear Sir/Madam

Using the ILP guidance for reduction of obtrusive light and as such the area in questing being Manchester City centre as an E4 Environmental Zone.  As such we have used the criteria of the E4 zone as the benchmark.

The Sky Glow (ULR) maximum for an E4 Environmental zone is 15% and as the calculations demonstrate the current lighting has a maximum ULR of 5% well below the fresh hold.

Light intrusion (into windows) the E4 Environmental Zone maximum permissible average lux level is 5Lux post 23.00 the calculations demonstrate a maximum average lux of any of the surrounding buildings to be approx. 3.4Lux, and thus complies.

The external lighting is also fully automated with Simmtronic control being used through out the project. This gives full control using “Dali communication” and provides various switching options, there will also be photocell and time clock as part of the installation.
The lighting output can also be trimmed back by dimming the lights if required

The accompanying documentation also gives a full break down on the columns and bollards alike providing various data sheets, lux levels, plots etc. etc. 

In theory the external lighting scheme has been selected due to being relatively free of light pollution or any overspill.

Overall, the scheme is in compliance with the ILP guidance notes for urban areas.



Best Regards

Mike Thomas 
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