www.luciongroup.com

# Technical Note – Post Construction Noise Assessment

Reliance Street, Manchester Presented to Be.EV

Issued: 2nd April 2025

Lucion Contract Reference 87687.544957

| Issue No. | Status | Issue Date | Comments | Author | Technical Review | Authorised |
| --- | --- | --- | --- | --- | --- | --- |
| 2 | Final Issue | 2nd April 2025 | Client Comments | Dan Boote Principal Acoustician | John Goodwin Director | Sarah Slater Associate |

# Context and Purpose

Lucion Delta-Simons Ltd (‘Lucion’) was instructed by Be.EV (the ‘Client’) to prepare a Noise Impact Assessment to confirm post construction to discharge a condition for a planning application (ref: 139860/JO/2024) for the development of an Electric Vehicle (EV) charging station consisting of 16 spaces, substation, and adjacent commercial space (the ‘Proposed Development’), located on land Reliance Street, Manchester (the ‘Site’).

This technical note has been submitted to Manchester City Council to discharge the requirements as set out under Condition 8 and Condition 9.

# Methodology

Following installation and commissioning of the proposed plant on the Site, noise measurements have been undertaken of the plant to determine any variation.

Noise levels were measured at 1m from the following plant items, on 28th March 2025:

  - A/C outdoor unit

  - Indoor unit extract louvre

  - Indoor unit intake louvre

As far as reasonably practicable, extraneous noise sources were paused out of the measurements to minimise their influence and to ensure the measured data is an accurate representation of noise from the plant. All measurements were undertaken with a Class 1 integrating sound level meter, which was field calibrated before and after the measurements.

These measurements were then compared to the predicted levels in the original noise impact assessment. Manufacturers data for the plant that was used in a previous is as follows:

  - A/C outdoor unit = 54dB LAeq at 1m

  - Indoor unit = 58dB LwA

    - At Extract Louvre1 = 55dB LAeq at 1m

    - At Intake Louvre1 = 50dB LAeq at 1m

# Results

The measurements of the plant installed on-site are as follows:

  - A/C outdoor unit = 55.0dB LAeq at 1m

  - Indoor unit extract louvre = 59.6dB LAeq at 1m

  - Indoor unit intake louvre = 54.4dB LAeq at 1m

The table below compares the measured data and the manufacturers data

## Table 1 - Measured and Manufacturers data

| Plant Item | Measured Noise Level, dB LAeq at 1m | Manufacturers Supplied Noise Level, dB LAeq at 1m | Difference2, dB LAeq at 1m |
| --- | --- | --- | --- |
| A/C Outdoor Unit | 55.0 | 54.0 | +1.0 |
| Indoor Unit at Extract Louvre | 59.6 | 55.01 | +4.6 |
| Indoor Unit at Intake Louvre | 54.4 | 50.01 | +4.4 |

As shown in the table above, measurements of the A/C Outdoor Unit are in general accordance with the manufacturers data. There is some variance in measured and manufacturer data for the Indoor Unit, however, this may be due to slight variations in ducting, or other noise sources influencing the measured levels.

# Verification

In order to comply with the planning condition, rated noise levels from the plant cannot exceed 46dB in the daytime and 37dB at night.

Given the Site location (adjacent to an existing major road) it is not possible to measure the plant noise level at the closest receptor in the absence of other noise sources. Therefore, to calculate the plant noise levels at the closest receptor, measure plant source noise levels have been used in a 3D noise model of the Site. The table below details the results of the calculations.

## Table 2 - Operational Site Noise

| Receptor | Period | Calculated Rating Noise Level at Receptor, LAr,T (dB) | Rating Noise Level Limit, LAr,T (dB) | Difference3 +/- (dB) |
| --- | --- | --- | --- | --- |
| R1 Ground Floor | Daytime | 37 | 46 | -9 |
|  | Night-time |  | 37 | 0 |
| R1 First Floor | Daytime | 37 | 46 | -9 |
|  | Night-time |  | 37 | 0 |
| R1 Second Floor | Daytime | 37 | 46 | -9 |

1 Calculated based on ducting layouts provided by the client

2 Calculated by subtracting the manufacturers data from the measured data

3 Calculated by subtracting the Rating Noise Level Limit from the Calculated Rating Noise Level

| Receptor | Period | Calculated Rating Noise Level at Receptor, LAr,T (dB) | Rating Noise Level Limit, LAr,T (dB) | Difference3 +/- (dB) |
| --- | --- | --- | --- | --- |
|  | Night-time |  | 37 | 0 |
| R1 Third Floor | Daytime | 36 | 46 | -10 |
|  | Night-time |  | 37 | -1 |

The table above shows that the rated noise level from the installed plant on the Site does not exceed the limits set out in the planning conditions for the Site. Therefore, it is considered that the condition can be discharged.