# VRV Selection

Project Report

Report details

Produced on:	3/6/2024

Application version:	2024.3.4.3

Project details

Project name:	 7152773 - BMG Manachester

Solution name:	VRV HR

Client Name:	Chapman Ventilation Ltd

Customer reference:

Quotation reference:

Project number:	1356720/1669675

The output of the VRV Xpress software is based on Daikin-genuine capacity tables that relate to the Japanese Industry Standard. The VRV Xpress software provides a selection of outdoor and indoor units with optimal efficiency to fit cooling and heating load requirements.

# Material list

| Model | Quantity | Description |
| --- | --- | --- |
| REYQ12U | 2 | REYQ-U (VRV IV) |
| REYQ14U | 1 | REYQ-U (VRV IV) |
| REYQ10U | 1 | REYQ-U (VRV IV) |
| BS4Q14AV1B | 1 | Branch selector unit |
| BS6Q14AV1B | 1 | Branch selector unit |
| BS10Q14AV1B | 1 | Branch selector unit |
| FXAQ32A | 1 | FXAQ-A - Wall mounted unit |
| FXSQ80A | 2 | FXSQ-A - Concealed ceiling unit with medium ESP |
| FXSQ100A | 4 | FXSQ-A - Concealed ceiling unit with medium ESP |
| FXSQ125A | 3 | FXSQ-A - Concealed ceiling unit with medium ESP |
| FXZQ40A | 7 | FXZQ-A - Fully flat cassette |
| BHFQ23P907A | 1 | Outdoor unit multi connection piping kit for 2 modules HR |
| BRC1H52W | 17 | Remote controller (white) |
| BYFQ60CW | 7 | New decoration panel (white) |

# Indoor unit details

## Table of abbreviations

| Abbreviation | Description |
| --- | --- |
| Name | Logical name of the device |
| FCU | Device model name |
| Tmp C | Indoor conditions in cooling |
| Rq TC | Required total cooling capacity |
| Max TC | Available total cooling capacity |
| Rq SC | Required sensible cooling capacity |
| Tevap | Evaporating temperature of indoor unit coil |
| Max SC | Available sensible cooling capacity |
| PIC | Power input in cooling mode @ 50Hz |
| Tmp H | Indoor temperature in heating |
| Rq HC | Required heating capacity |
| Max HC | Available heating capacity |
| PIH | Power input in heating mode @ 50Hz |
| Sound | Sound pressure level low and high |
| PS | Power supply (voltage and phases) |
| MCA | Minimum Circuit Amps |
| MFA | Maxium Fuse Amps |
| WxHxD | WidthxHeightxDepth |
| Weight | Weight of the device |

CU 1-1 - REYQ12U

Capacity data at conditions and connection ratio (104) as entered

| Name | FCU | Cooling |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Tmp C | Rq TC | Max TC | Rq SC | Tevap | Max SC | PIC |
|  |  | °C (DBT/RH) | kW | kW | kW | °C | kW | kW |
| AC 1-1 | FXZQ40A | 23.0/50% | n/a | 3.7 | n/a | 6.0 | 2.9 | 0.029 |
| AC 1-2 | FXAQ32A | 23.0/50% | n/a | 3.0 | n/a | 6.0 | 2.4 | 0.030 |
| AC 1-3 | FXZQ40A | 23.0/50% | n/a | 3.7 | n/a | 6.0 | 2.9 | 0.029 |
| AC 1-4 | FXZQ40A | 23.0/50% | n/a | 3.7 | n/a | 6.0 | 2.9 | 0.029 |
| AC 1-5 | FXZQ40A | 23.0/50% | n/a | 3.7 | n/a | 6.0 | 2.9 | 0.029 |
| AC 1-6 | FXZQ40A | 23.0/50% | n/a | 3.7 | n/a | 6.0 | 2.9 | 0.029 |
| AC 1-7 | FXZQ40A | 23.0/50% | n/a | 3.7 | n/a | 6.0 | 2.9 | 0.029 |
| AC 1-8 | FXZQ40A | 23.0/50% | n/a | 3.7 | n/a | 6.0 | 2.9 | 0.029 |
|  |  |  | 0.0 |  |  |  |  |  |

| Name | FCU | Heating |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Tmp H | Rq HC | Max HC | PIH |
|  |  | °C | kW | kW | kW |
| AC 1-1 | FXZQ40A | 20.0 | n/a | 5.0 | 0.029 |
| AC 1-2 | FXAQ32A | 20.0 | n/a | 4.0 | 0.040 |
| AC 1-3 | FXZQ40A | 20.0 | n/a | 5.0 | 0.029 |
| AC 1-4 | FXZQ40A | 20.0 | n/a | 5.0 | 0.029 |
| AC 1-5 | FXZQ40A | 20.0 | n/a | 5.0 | 0.029 |
| AC 1-6 | FXZQ40A | 20.0 | n/a | 5.0 | 0.029 |
| AC 1-7 | FXZQ40A | 20.0 | n/a | 5.0 | 0.029 |
| AC 1-8 | FXZQ40A | 20.0 | n/a | 5.0 | 0.029 |
|  |  |  | n/a |  |  |

| Name | FCU | Room | Sound | PS | MCA | MFA | WxHxD | Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | dBA |  | A |  | mm | kg |
| AC 1-1 | FXZQ40A |  | 28 - 37 | 220V 1ph | 0.4 | Factory Std | 575 x 260 x 575 | 16.5 |
| AC 1-2 | FXAQ32A |  | 29 - 38 | 230V 1ph | 0.4 | Factory Std | 795 x 290 x 266 | 12.0 |
| AC 1-3 | FXZQ40A |  | 28 - 37 | 220V 1ph | 0.4 | Factory Std | 575 x 260 x 575 | 16.5 |
| AC 1-4 | FXZQ40A |  | 28 - 37 | 220V 1ph | 0.4 | Factory Std | 575 x 260 x 575 | 16.5 |
| AC 1-5 | FXZQ40A |  | 28 - 37 | 220V 1ph | 0.4 | Factory Std | 575 x 260 x 575 | 16.5 |
| AC 1-6 | FXZQ40A |  | 28 - 37 | 220V 1ph | 0.4 | Factory Std | 575 x 260 x 575 | 16.5 |
| AC 1-7 | FXZQ40A |  | 28 - 37 | 220V 1ph | 0.4 | Factory Std | 575 x 260 x 575 | 16.5 |
| AC 1-8 | FXZQ40A |  | 28 - 37 | 220V 1ph | 0.4 | Factory Std | 575 x 260 x 575 | 16.5 |

Outdoor vs. indoor position

Outdoor unit placed at the same level as the indoor units.

CU 2-1 - REYQ22U = REYQ12U + REYQ10U

Capacity data at conditions and connection ratio (102) as entered

| Name | FCU | Cooling |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Tmp C | Rq TC | Max TC | Rq SC | Tevap | Max SC | PIC |
|  |  | °C (DBT/RH) | kW | kW | kW | °C | kW | kW |
| AC 2-1 | FXSQ80A | 23.0/50% | n/a | 7.3 | n/a | 6.0 | 5.6 | 0.135 |
| AC 2-2 | FXSQ80A | 23.0/50% | n/a | 7.3 | n/a | 6.0 | 5.6 | 0.135 |
| AC 2-3 | FXSQ100A | 23.0/50% | n/a | 9.2 | n/a | 6.0 | 7.1 | 0.173 |
| AC 2-4 | FXSQ100A | 23.0/50% | n/a | 9.2 | n/a | 6.0 | 7.1 | 0.173 |
| AC 2-5 | FXSQ100A | 23.0/50% | n/a | 9.2 | n/a | 6.0 | 7.1 | 0.173 |
| AC 2-6 | FXSQ100A | 23.0/50% | n/a | 9.2 | n/a | 6.0 | 7.1 | 0.173 |
|  |  |  | 0.0 |  |  |  |  |  |

| Name | FCU | Heating |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Tmp H | Rq HC | Max HC | PIH |
|  |  | °C | kW | kW | kW |
| AC 2-1 | FXSQ80A | 20.0 | n/a | 10.0 | 0.135 |
| AC 2-2 | FXSQ80A | 20.0 | n/a | 10.0 | 0.135 |
| AC 2-3 | FXSQ100A | 20.0 | n/a | 12.5 | 0.173 |
| AC 2-4 | FXSQ100A | 20.0 | n/a | 12.5 | 0.173 |
| AC 2-5 | FXSQ100A | 20.0 | n/a | 12.5 | 0.173 |
| AC 2-6 | FXSQ100A | 20.0 | n/a | 12.5 | 0.173 |
|  |  |  | n/a |  |  |

| Name | FCU | Room | Sound | PS | MCA | MFA | WxHxD | Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | dBA |  | A |  | mm | kg |
| AC 2-1 | FXSQ80A |  | 29 - 35 | 220V 1ph | 1.9 | Factory Std | 1,000 x 245 x 800 | 36.5 |
| AC 2-2 | FXSQ80A |  | 29 - 35 | 220V 1ph | 1.9 | Factory Std | 1,000 x 245 x 800 | 36.5 |
| AC 2-3 | FXSQ100A |  | 31 - 36 | 220V 1ph | 2.4 | Factory Std | 1,400 x 245 x 800 | 46.0 |
| AC 2-4 | FXSQ100A |  | 31 - 36 | 220V 1ph | 2.4 | Factory Std | 1,400 x 245 x 800 | 46.0 |
| AC 2-5 | FXSQ100A |  | 31 - 36 | 220V 1ph | 2.4 | Factory Std | 1,400 x 245 x 800 | 46.0 |
| AC 2-6 | FXSQ100A |  | 31 - 36 | 220V 1ph | 2.4 | Factory Std | 1,400 x 245 x 800 | 46.0 |

Outdoor vs. indoor position

Outdoor unit placed at the same level as the indoor units.

CU 3-1 - REYQ14U

Capacity data at conditions and connection ratio (107) as entered

| Name | FCU | Cooling |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Tmp C | Rq TC | Max TC | Rq SC | Tevap | Max SC | PIC |
|  |  | °C (DBT/RH) | kW | kW | kW | °C | kW | kW |
| AC 3-1 | FXSQ125A | 23.0/50% | n/a | 11.5 | n/a | 6.0 | 8.8 | 0.237 |
| AC 3-2 | FXSQ125A | 23.0/50% | n/a | 11.5 | n/a | 6.0 | 8.8 | 0.237 |
| AC 3-3 | FXSQ125A | 23.0/50% | n/a | 11.5 | n/a | 6.0 | 8.8 | 0.237 |
|  |  |  | 0.0 |  |  |  |  |  |

| Name | FCU | Heating |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Tmp H | Rq HC | Max HC | PIH |
|  |  | °C | kW | kW | kW |
| AC 3-1 | FXSQ125A | 20.0 | n/a | 16.0 | 0.237 |
| AC 3-2 | FXSQ125A | 20.0 | n/a | 16.0 | 0.237 |
| AC 3-3 | FXSQ125A | 20.0 | n/a | 16.0 | 0.237 |
|  |  |  | n/a |  |  |

| Name | FCU | Room | Sound | PS | MCA | MFA | WxHxD | Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | dBA |  | A |  | mm | kg |
| AC 3-1 | FXSQ125A |  | 33 - 39 | 220V 1ph | 2.6 | Factory Std | 1,400 x 245 x 800 | 47.0 |
| AC 3-2 | FXSQ125A |  | 33 - 39 | 220V 1ph | 2.6 | Factory Std | 1,400 x 245 x 800 | 47.0 |
| AC 3-3 | FXSQ125A |  | 33 - 39 | 220V 1ph | 2.6 | Factory Std | 1,400 x 245 x 800 | 47.0 |

Outdoor vs. indoor position

Outdoor unit placed at the same level as the indoor units.

# Outdoor unit details

## Table of abbreviations

| Abbreviation | Description |
| --- | --- |
| Name | Logical name of the device |
| Model | Device model name |
| ▼ | Optimized selection: Smaller outdoor model selected than standard proposed model |
| CR | Connection ratio |
| Tmp C | Outdoor conditions in cooling |
| WFR | Water flow per outdoor unit module |
| CC | Available cooling capacity |
| Rq CC | Required cooling capacity |
| PIC | Power input in cooling mode |
| InC | Water inlet temperature in cooling mode |
| OutC | Water outlet temperature in cooling mode |
| Tmp H | Outdoor conditions in heating (dry bulb temp. / RH) |
| HC | Available heating capacity (integrated heating capacity) |
| Rq HC | Required heating capacity |
| PIH | Power input in heating mode |
| InH | Water inlet temperature in heating mode |
| OutH | Water outlet temperature in heating mode |
| Piping | Largest distance from indoor unit to outdoor unit |
| Bse Refr | Standard factory refrigerant charge (16.4ft actual piping length) excluding extra refrigerant charge. For calculation of extra refrigerant charge refer to the databook |
| Ex Refr | Extra refrigerant charge |
| PS | Power supply (voltage and phases) |
| MCA | Minimum Circuit Amps |
| MFA | Maxium Fuse Amps |
| FLA | Fan Motor Input |
| RLA | Nominal Running Amps |
| WxHxD | WidthxHeightxDepth |
| Weight | Weight of the device |
| EER | EER value at nominal condition |
| EER2 | EER2 value at nominal condition |
| IEER | IEER value at nominal condition |
| COP47 | COP value at nominal condition and at ambient temperature of 8°C |
| COP17 | COP value at nominal condition and at ambient temperature of -8°C |

## Outdoor details

| Name | Model | CR | Cooling |  |  | Heating |  |  | Piping |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Tmp C | CC | Rq CC | Tmp H | HC | Rq HC |  |
|  |  | % | °C | kW | kW | °C (DBT/RH) | kW | kW | m |
| CU 1-1 | REYQ12U▼ | 103.8 | 35.0 | 27.4 | 20.1 | -5.0/80% | 26.5 | 27.3 | 7.5 |
| CU 2-1 | REYQ22U▼ | 101.8 | 35.0 | 49.3 | 51.4 | -5.0/80% | 50.2 | 70.0 | 7.5 |
| CU 3-1 | REYQ14U▼ | 107.1 | 35.0 | 33.7 | 24.2 | -5.0/80% | 32.6 | 33.6 | 7.5 |

| Name | Model | PS | MCA | MFA | RLA | FLA | WxHxD | Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | A | A | A | A | mm | kg |
| CU 1-1 | REYQ12U | 400V 3Nph | 24.0 | 32.0 | 13.8 | 1.5 | 930 x 1,685 x 765 | 230.0 |
| BC 1-1 | BS10Q14AV1B | 230V 1ph | 1.0 | 15.0 |  |  | 820 x 298 x 430 | 42.0 |
| CU 2-1 | REYQ22U | 400V 3Nph |  |  |  |  |  |  |
| A | - REYQ12U |  | 24.0 | 32.0 | 13.8 | 1.5 | 930 x 1,685 x 765 | 230.0 |
| B | - REYQ10U |  | 22.0 | 25.0 | 10.5 | 1.3 | 930 x 1,685 x 765 | 230.0 |
| BC 2-1 | BS6Q14AV1B | 230V 1ph | 0.6 | 15.0 |  |  | 580 x 298 x 430 | 28.0 |
| CU 3-1 | REYQ14U | 400V 3Nph | 27.0 | 32.0 | 15.6 | 1.8 | 1,240 x 1,685 x 765 | 314.0 |
| BC 3-1 | BS4Q14AV1B | 230V 1ph | 0.4 | 15.0 |  |  | 370 x 298 x 430 | 22.0 |

## Sound Data

| Name | Model | Sound Power |  | Sound Pressure |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Cooling | Heating | Cooling | Heating |
|  |  | dBA | dBA | dBA | dBA |
| CU 1-1 | REYQ12U | 83 | 65 | 61 | - |
| CU 2-1 | REYQ22U | 85 | 68 | 63 | - |
| CU 3-1 | REYQ14U | 81 | 68 | 60 | - |

## Seasonal Efficiency

| Name | Model | ηs,h heating | ηs,c cooling | SCOP | SEER | CSPF |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | % | % |  |  |  |
| CU 1-1 | REYQ12U | 183.8 | 257.0 | 4.70 | 6.50 | - |
| CU 2-1 | REYQ22U | 178.5 | 260.4 | 4.50 | 6.60 | - |
| CU 3-1 | REYQ14U | 168.3 | 255.8 | 4.30 | 6.50 | - |

For more information go to: https://energylabel.daikin.eu/.

## Refrigerant information

| Name | Model | Refrigerant type | GWP | Base charge kg | Extra charge kg | Total refrigerant charge kg | Total CO2 equivalent tonnes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CU 1-1 | REYQ12U | R410A | 2087.5 | 9.90 | unknown | unknown | 20.67 |
| CU 2-1 | REYQ22U | R410A | 2087.5 | 19.70 | unknown | unknown | 41.12 |
| CU 3-1 | REYQ14U | R410A | 2087.5 | 11.80 | unknown | unknown | 24.63 |

The system(s) contain fluorinated greenhouse gases.

TCO2 equivalent is calculated only considering the base refrigerant charge. Depending on the field pipe length extra refrigerant needs to be added which will increase the TCO2 equivalent.

CU 1-1 - REYQ12U

| Model | Quantity | Description |
| --- | --- | --- |
| REYQ12U | 1 | REYQ-U (VRV IV) |
| BS10Q14AV1B | 1 | Branch selector unit |
| FXAQ32A | 1 | FXAQ-A - Wall mounted unit |
| FXZQ40A | 7 | FXZQ-A - Fully flat cassette |
| BRC1H52W | 8 | Remote controller (white) |
| BYFQ60CW | 7 | New decoration panel (white) |

Refrigerant information

| Refrigerant type | GWP | Base charge kg | Extra charge kg | Total refrigerant charge kg | Total CO2 equivalent tonnes |
| --- | --- | --- | --- | --- | --- |
| R410A | 2087.5 | 9.90 | unknown | unknown | 20.67 |

The system(s) contain fluorinated greenhouse gases.

TCO2 equivalent is calculated only considering the base refrigerant charge. Depending on the field pipe length extra refrigerant needs to be added which will increase the TCO2 equivalent.

Remarks

Chosen outdoor unit size differs from default proposed size. Be aware that this might lead to reduced comfort levels, increased noise levels, wear and tear. In case of doubt, contact your sales representative.

Pipe capacities

| Maximum Connection Index | Diameters |
| --- | --- |
| 149.9 | 3/8"x5/8"x1/2" |
| 199.9 | 3/8"x3/4"x5/8" |
| 289.9 | 3/8"x7/8"x3/4" |
| 419.9 | 1/2"x1 1/8"x3/4" |
| 639.9 | 5/8"x1 1/8"x1 1/8" |
| 919.9 | 3/4"x1 3/8"x1 1/8" |
| > 919.9 | 3/4"x1 5/8"x1 1/8" |
| Main pipe size up | 5/8"x1 1/8"x3/4" |

Remarks

Please make sure to provide a drain pipe connection to each multi BS-box in the system.

Piping limitations

| Description | Value |
| --- | --- |
| Maximum total length | 1,000.0m |
| Maximum longest actual length | 165.0m |
| Maximum longest equivalent length | 190.0m |
| Maximum main pipe length (size up of main pipe required if longer) | - |
| Maximum length first branch to indoor unit(size up of intermediate pipes required if longer) | 40.0m |
| Maximum length first branch to indoor unit | 90.0m |
| Maximum length of indoor units to nearest branch | 40.0m |
| Maximum length difference between longest and shortest distance to indoor units | 40.0m |
| Maximum height difference, outdoor unit below indoor units | 90.0m |
| Minimum connection ratio, outdoor unit below indoor units | - |
| Maximum height difference, outdoor unit above indoor units | 90.0m |
| Minimum connection ratio, outdoor unit above indoor units | - |
| Maximum height difference in technical cooling, outdoor unit below indoor units | 90.0m |
| Maximum height difference in technical cooling, outdoor unit above indoor units | 90.0m |
| Maximum height difference between indoor units | 30.0m |
| Connection ratio range | 50.0% - 200.0% |
| Refrigerant pipe diameters | 5/8" (liquid) x 1 1/8" (gas) x 3/4" (discharge) |
| Maximum equivalent length from BP unit or VRV indoor to VRV REFNET (size up of intermediate pipes required if longer) | - |
| Maximum equivalent length from BP unit or VRV indoor to VRV REFNET | 90.0m |
| Maximum actual length between CM and HM | - |
| Maximum height difference between CM and HM | - |

CU 2-1 - REYQ22U = REYQ12U + REYQ10U

| Model | Quantity | Description |
| --- | --- | --- |
| REYQ12U | 1 | REYQ-U (VRV IV) |
| REYQ10U | 1 | REYQ-U (VRV IV) |
| BS6Q14AV1B | 1 | Branch selector unit |
| FXSQ80A | 2 | FXSQ-A - Concealed ceiling unit with medium ESP |
| FXSQ100A | 4 | FXSQ-A - Concealed ceiling unit with medium ESP |
| BHFQ23P907A | 1 | Outdoor unit multi connection piping kit for 2 modules HR |
| BRC1H52W | 6 | Remote controller (white) |

Refrigerant information

| Refrigerant type | GWP | Base charge kg | Extra charge kg | Total refrigerant charge kg | Total CO2 equivalent tonnes |
| --- | --- | --- | --- | --- | --- |
| R410A | 2087.5 | 19.70 | unknown | unknown | 41.12 |

The system(s) contain fluorinated greenhouse gases.

TCO2 equivalent is calculated only considering the base refrigerant charge. Depending on the field pipe length extra refrigerant needs to be added which will increase the TCO2 equivalent.

Remarks

Chosen outdoor unit size differs from default proposed size. Be aware that this might lead to reduced comfort levels, increased noise levels, wear and tear. In case of doubt, contact your sales representative.

Pipe capacities

| Maximum Connection Index | Diameters |
| --- | --- |
| 149.9 | 3/8"x5/8"x1/2" |
| 199.9 | 3/8"x3/4"x5/8" |
| 289.9 | 3/8"x7/8"x3/4" |
| 419.9 | 1/2"x1 1/8"x3/4" |
| 639.9 | 5/8"x1 1/8"x1 1/8" |
| 919.9 | 3/4"x1 3/8"x1 1/8" |
| > 919.9 | 3/4"x1 5/8"x1 1/8" |
| Main pipe size up | 3/4"x1 1/8"x1 1/8" |

Remarks

Please make sure to provide a drain pipe connection to each multi BS-box in the system.

Sufficient distance should be respected between the modules according to the service & operation space rules as mentioned in the databook.

Piping limitations

| Description | Value |
| --- | --- |
| Maximum total length | 1,000.0m |
| Maximum longest actual length | 165.0m |
| Maximum longest equivalent length | 190.0m |
| Maximum main pipe length (size up of main pipe required if longer) | - |
| Maximum length first branch to indoor unit(size up of intermediate pipes required if longer) | 40.0m |
| Maximum length first branch to indoor unit | 90.0m |
| Maximum length of indoor units to nearest branch | 40.0m |
| Maximum length difference between longest and shortest distance to indoor units | 40.0m |
| Maximum height difference, outdoor unit below indoor units | 90.0m |
| Minimum connection ratio, outdoor unit below indoor units | - |
| Maximum height difference, outdoor unit above indoor units | 90.0m |
| Minimum connection ratio, outdoor unit above indoor units | - |
| Maximum height difference in technical cooling, outdoor unit below indoor units | 90.0m |
| Maximum height difference in technical cooling, outdoor unit above indoor units | 90.0m |
| Maximum height difference between indoor units | 30.0m |
| Connection ratio range | 50.0% - 200.0% |
| Refrigerant pipe diameters | 3/4" (liquid) x 1 1/8" (gas) x 1 1/8" (discharge) |
| Maximum equivalent length from BP unit or VRV indoor to VRV REFNET (size up of intermediate pipes required if longer) | - |
| Maximum equivalent length from BP unit or VRV indoor to VRV REFNET | 90.0m |
| Maximum actual length between CM and HM | - |
| Maximum height difference between CM and HM | - |

CU 3-1 - REYQ14U

| Model | Quantity | Description |
| --- | --- | --- |
| REYQ14U | 1 | REYQ-U (VRV IV) |
| BS4Q14AV1B | 1 | Branch selector unit |
| FXSQ125A | 3 | FXSQ-A - Concealed ceiling unit with medium ESP |
| BRC1H52W | 3 | Remote controller (white) |

Refrigerant information

| Refrigerant type | GWP | Base charge kg | Extra charge kg | Total refrigerant charge kg | Total CO2 equivalent tonnes |
| --- | --- | --- | --- | --- | --- |
| R410A | 2087.5 | 11.80 | unknown | unknown | 24.63 |

The system(s) contain fluorinated greenhouse gases.

TCO2 equivalent is calculated only considering the base refrigerant charge. Depending on the field pipe length extra refrigerant needs to be added which will increase the TCO2 equivalent.

Remarks

Chosen outdoor unit size differs from default proposed size. Be aware that this might lead to reduced comfort levels, increased noise levels, wear and tear. In case of doubt, contact your sales representative.

Pipe capacities

| Maximum Connection Index | Diameters |
| --- | --- |
| 149.9 | 3/8"x5/8"x1/2" |
| 199.9 | 3/8"x3/4"x5/8" |
| 289.9 | 3/8"x7/8"x3/4" |
| 419.9 | 1/2"x1 1/8"x3/4" |
| 639.9 | 5/8"x1 1/8"x1 1/8" |
| 919.9 | 3/4"x1 3/8"x1 1/8" |
| > 919.9 | 3/4"x1 5/8"x1 1/8" |
| Main pipe size up | 5/8"x1 1/8"x7/8" |

Remarks

Please make sure to provide a drain pipe connection to each multi BS-box in the system.

Piping limitations

| Description | Value |
| --- | --- |
| Maximum total length | 1,000.0m |
| Maximum longest actual length | 165.0m |
| Maximum longest equivalent length | 190.0m |
| Maximum main pipe length (size up of main pipe required if longer) | - |
| Maximum length first branch to indoor unit(size up of intermediate pipes required if longer) | 40.0m |
| Maximum length first branch to indoor unit | 90.0m |
| Maximum length of indoor units to nearest branch | 40.0m |
| Maximum length difference between longest and shortest distance to indoor units | 40.0m |
| Maximum height difference, outdoor unit below indoor units | 90.0m |
| Minimum connection ratio, outdoor unit below indoor units | - |
| Maximum height difference, outdoor unit above indoor units | 90.0m |
| Minimum connection ratio, outdoor unit above indoor units | - |
| Maximum height difference in technical cooling, outdoor unit below indoor units | 90.0m |
| Maximum height difference in technical cooling, outdoor unit above indoor units | 90.0m |
| Maximum height difference between indoor units | 30.0m |
| Connection ratio range | 50.0% - 200.0% |
| Refrigerant pipe diameters | 5/8" (liquid) x 1 1/8" (gas) x 7/8" (discharge) |
| Maximum equivalent length from BP unit or VRV indoor to VRV REFNET (size up of intermediate pipes required if longer) | - |
| Maximum equivalent length from BP unit or VRV indoor to VRV REFNET | 90.0m |
| Maximum actual length between CM and HM | - |
| Maximum height difference between CM and HM | - |

# Piping diagrams

Piping CU 1-1

Piping

Warning: The pipe diameter values are purely indicative. Depending on the required pipe lengths, a different pipe diameter might be required.

Piping CU 2-1

Piping

Warning: The pipe diameter values are purely indicative. Depending on the required pipe lengths, a different pipe diameter might be required.

Piping CU 3-1

Piping

Warning: The pipe diameter values are purely indicative. Depending on the required pipe lengths, a different pipe diameter might be required.

# Wiring diagrams

Wiring CU 1-1

Remarks

P1P2 = 0,75 - 1,25 mm2, max 500m length -  always refer to local code for further information.

F1F2 IN/OUT transmission wiring, use 2-core wires of 0,75 to 1,25 mm² size cables, without shield (but shielded cable can be used if required by local regulations and standards).

Note: The shield should only be earthed at outdoor unit side, not at the indoor units!

Wiring CU 2-1

Remarks

P1P2 = 0,75 - 1,25 mm2, max 500m length -  always refer to local code for further information.

F1F2 IN/OUT transmission wiring, use 2-core wires of 0,75 to 1,25 mm² size cables, without shield (but shielded cable can be used if required by local regulations and standards).

Note: The shield should only be earthed at outdoor unit side, not at the indoor units!

Wiring CU 3-1

Remarks

P1P2 = 0,75 - 1,25 mm2, max 500m length -  always refer to local code for further information.

F1F2 IN/OUT transmission wiring, use 2-core wires of 0,75 to 1,25 mm² size cables, without shield (but shielded cable can be used if required by local regulations and standards).

Note: The shield should only be earthed at outdoor unit side, not at the indoor units!

# Best Practices

## Multi BS-box

- Install the multi BS-box on a location where the refrigerant noise cannot disturb the room occupants

- To avoid that refrigerant noise disturbs the people in the room, keep at least 5m piping length between the occupied room and the multi BS unit (See figure)

- If there is no false ceiling in the occupied room, please add sound insulation around the piping between the multi BS-box and indoor unit, or keep much longer length between multi BS-box unit and occupied room (See figure)

## Residual Current Circuit Breaker

For better protection of installations against the risk of fire, power supply of indoor and outdoor units must be protected with a Residual Current Circuit Breaker. For protection against fire, we recommend a sensitivity of 300mA. The selected RCCB should be of the type B, suitable for inverter devices and indicated by the symbols here below. Further electrical characteristics of the RCCB must be selected in accordance with local regulation.

For a complete list of all required safety precautions, warnings and attention points, please consult the “general safety precautions manual” delivered with the unit.