## Sheet1
Remediation report
project information details :- |  | DK Adana City labs Hathersage Rd Manchester 19 02 24
Section | Upstream node | Downstream node | Inspection Direction | Diameter | Material | Observation on defect | Remark by operator | Meterage | Grade | Remedial requirements | Cost of remediation
specialist hpwj clean
5 | 5 | IFWMH1.1 | Downstream | 100 | Polyvinyl chloride | Start node, rodding eye, reference: 5 |  | 0
5 | 5 | IFWMH1.1 | Downstream | 100 | Polyvinyl chloride | Water level, 0% of the vertical dimension |  | 0
5 | 5 | IFWMH1.1 | Downstream | 100 | Polyvinyl chloride | Line deviates left |  | 0.69
5 | 5 | IFWMH1.1 | Downstream | 100 | Polyvinyl chloride | Attached deposits, encrustation from 4 o'clock to 5 o'clock, 5% cross-sectional area loss |  | 3.21
5 | 5 | IFWMH1.1 | Downstream | 100 | Polyvinyl chloride | Finish node, manhole, reference: IFWMH1.1 |  | 9.56
7 | 7 | IFWMH1.2 | Downstream | 100 | Polyvinyl chloride | Start node, rodding eye, reference: 7 |  | 0 |  | hpwj clean
7 | 7 | IFWMH1.2 | Downstream | 100 | Polyvinyl chloride | Water level, 0% of the vertical dimension |  | 0
7 | 7 | IFWMH1.2 | Downstream | 100 | Polyvinyl chloride | Settled deposits, coarse, 5% cross-sectional area loss |  | 0.8
7 | 7 | IFWMH1.2 | Downstream | 100 | Polyvinyl chloride | Line deviates left |  | 1.1
7 | 7 | IFWMH1.2 | Downstream | 100 | Polyvinyl chloride | Junction at 12 o'clock, 100mm dia | POP UP 16 | 6.16
7 | 7 | IFWMH1.2 | Downstream | 100 | Polyvinyl chloride | Finish node, manhole, reference: IFWMH1.2 |  | 12.14
18 | 18 | CARRIER | Downstream | 100 | Polyvinyl chloride | Start node, rodding eye, reference: 18 | POP UP | 0 |  | specialist hpwj clean
18 | 18 | CARRIER | Downstream | 100 | Polyvinyl chloride | Water level, 5% of the vertical dimension |  | 0
18 | 18 | CARRIER | Downstream | 100 | Polyvinyl chloride | Line deviates left |  | 0.61
18 | 18 | CARRIER | Downstream | 100 | Polyvinyl chloride | Attached deposits, encrustation at 7 o'clock, 5% cross-sectional area loss |  | 2.53
18 | 18 | CARRIER | Downstream | 100 | Polyvinyl chloride | Line deviates left |  | 2.88
18 | 18 | CARRIER | Downstream | 100 | Polyvinyl chloride | Finish node, major connection without manhole, reference: CARRIER | JONS CARRIER TO MH | 3.3
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Start node, rodding eye, reference: 23 |  | 0 |  | hpwj clean
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Water level, 0% of the vertical dimension |  | 0
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Settled deposits, hard or compacted, 5% cross-sectional area loss | STONES UNABLE TO JET | 0.53
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Junction at 3 o'clock, 100mm dia | 24 POP UP | 0.95
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Junction at 3 o'clock, 100mm dia | 25 POP UP | 2.07
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Settled deposits, hard or compacted, 5% cross-sectional area loss | STONES | 6.64
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Line deviates right |  | 9.92
23 | 23 | CARRIER | Downstream | 100 | Vitrified clay | Finish node, major connection without manhole, reference: CARRIER |  | 10.38
25 | 25 | CARRIER | Downstream | 100 | Vitrified clay | Start node, rodding eye, reference: 25 |  | 0 |  | hpwj clean
25 | 25 | CARRIER | Downstream | 100 | Vitrified clay | Water level, 0% of the vertical dimension |  | 0.01
25 | 25 | CARRIER | Downstream | 100 | Vitrified clay | Settled deposits, coarse, 5% cross-sectional area loss |  | 0.3
25 | 25 | CARRIER | Downstream | 100 | Vitrified clay | Finish node, major connection without manhole, reference: CARRIER |  | 0.71
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Start node, rodding eye, reference: 38 |  | 0 |  | hpwj clean - 1 x patch lining works
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Water level, 0% of the vertical dimension |  | 0
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Settled deposits, coarse, 5% cross-sectional area loss |  | 2.04
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Junction at 3 o'clock, 300mm dia | 37 POP UP | 2.61
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Joint displaced, medium |  | 5.91
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Pipe material changes to polyethylene at this point |  | 6.2
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Settled deposits, coarse, 5% cross-sectional area loss |  | 8.29
37 | 38 | ATT TANK | Downstream | 300 | Vitrified clay | Finish node, major connection without manhole, reference: ATT TANK | JOINS TANK | 10.76
39 | FWMH2 | 27 | Downstream | 100 | Vitrified clay | Start node, manhole, reference: FWMH2 |  | 0 |  | 1 x patch lining works
39 | FWMH2 | 27 | Downstream | 100 | Vitrified clay | Water level, 5% of the vertical dimension |  | 0
39 | FWMH2 | 27 | Downstream | 100 | Vitrified clay | Pipe size changes, new size(s), 100mm high, 100mm wide |  | 0.1
39 | FWMH2 | 27 | Downstream | 100 | Vitrified clay | Joint displaced, medium |  | 14.55
39 | FWMH2 | 27 | Downstream | 100 | Vitrified clay | Junction at 2 o'clock, 100mm dia |  | 17.58
39 | FWMH2 | 27 | Downstream | 100 | Vitrified clay | Line deviates up | IN REST | 19.55
39 | FWMH2 | 27 | Downstream | 100 | Vitrified clay | Finish node, other special chamber, reference: 27 | IN REST BEND | 19.55
41 | IFWMH1.2 | EX FWMH | Downstream | 100 | Polyvinyl chloride | Start node, manhole, reference: IFWMH1.2 |  | 0 |  | 1 x patch lining works
41 | IFWMH1.2 | EX FWMH | Downstream | 100 | Polyvinyl chloride | Water level, 5% of the vertical dimension |  | 0
41 | IFWMH1.2 | EX FWMH | Downstream | 100 | Polyvinyl chloride | Line deviates left |  | 0.41
41 | IFWMH1.2 | EX FWMH | Downstream | 100 | Polyvinyl chloride | Finish node, major connection without manhole, reference: carrier | joins carrier | 3.22
41 | IFWMH1.2 | EX FWMH | Downstream | 100 | Polyvinyl chloride | Water level, 15% of the vertical dimension |  | 20.13
41 | IFWMH1.2 | EX FWMH | Downstream | 100 | Polyvinyl chloride | Joint displaced, medium |  | 22.36
41 | IFWMH1.2 | EX FWMH | Downstream | 100 | Polyvinyl chloride | Finish node, manhole, reference: EX FWMH |  | 23.06
43 | IFWMH3.0 | MHFW2 | Upstream | 150 | Vitrified clay | Start node, manhole, reference: MHFW2 |  | 0 |  | hpwj clean
43 | IFWMH3.0 | MHFW2 | Upstream | 150 | Vitrified clay | Water level, 5% of the vertical dimension |  | 0
43 | IFWMH3.0 | MHFW2 | Upstream | 150 | Vitrified clay | Settled deposits, coarse, 5% cross-sectional area loss, start |  | 17.7
43 | IFWMH3.0 | MHFW2 | Upstream | 150 | Vitrified clay | Settled deposits, coarse, 5% cross-sectional area loss, finish |  | 20.03
43 | IFWMH3.0 | MHFW2 | Upstream | 150 | Vitrified clay | Finish node, manhole, reference: IFWMH3.0 |  | 20.19
NRCWWS Ltd
Unit D, Russell Road, Rock Ferry, CH42 1LU TEL: 0151 643 0800 nrcwws.co.uk