
[image: image1.jpg]=

Blocked



                      
10 Eltham Drive,
Urmston, Manchester
M41 7NB                                                                                                         
Tel: 0161 286 9903   Fax: 0161 374 9346

Mobile: 07813 711 636                                                                  
www.blockeddrainsnorthwest.co.uk
                       DRAIN REPORT   
                                                                                                        10.12.2024
Withington Hospital 
SWE1
CCTV survey carried out from existing M/H SWE1 to main M/H on Nell Lane. 

Flow rate at the time of survey 10%
Pipe condition good 

Slight obstruction in the drains @6m downstream, this was moved when the camera was pushed past. This is Not causing any restriction to the flow of the drain.

Surveying down to 12.5m, this is where the pipe drops down to the M/H on Nell lane.
The pipe is in good condition with no problems to report.

