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                      DRAIN REPORT   
                                                                                                        16.07.2024
Withington Hospital 
Line clean of the drainage system 100mm clay 
From:

FWMH 1.7 to 1.6 cleaned

FWMH 1.6 to 1.5 cleaned 

FWMH 1.5 to 1.4 cleaned

FWMH 1.4 to 1.3 cleaned slight holding of water 5% no obstructions
FWMH 1.3 to 1.2 cleaned holding water camera submerged no debris 10% flat drain
FWMH 1.2 to 1.0 cleaned flat drain water holding 5%
Displaced joint 28.7m with the flow of the drains not causing any back up or blockages

FWMH 1.0 to E01 to road 99% of roots removed but still has fines sticking out through the joint these are not restricting any flow as they are at 10 o’clock position.

At 8m downstream before the drop there is a displaced joint this was more noticeable when the roots were cut out 

