Withington CDC - Meeting with UU regarding Planning Condition 
19.12.24 @10am

Tony Fear – MFT / Mace
Anthony Laithwaite – UU
Olivia Carr - Turley 
Jordan Farrely - CCS

Meeting to review Pre-commencement planning condition 11 (below) of the new Withington CDC.

11) Notwithstanding the approved documents and drawings, prior to installation of any surface water drainage at the site an updated scheme for surface water drainage works 140400/JO/2024 Page 6 of 12 in accordance with Non Statutory Technical Standards for Sustainable Drainage Systems (March 2015) or any subsequent replacements national standards and details shall be submitted to and approved in writing by the City Council as Local Planning Authority. The approved drainage system shall be implemented in accordance with the approved detailed design, prior to the first use of the building. The submitted scheme shall include:
· Progression through the drainage hierarchy shall be evidence based and supported by site investigation. Results of ground investigation carried out under Building Research Establishment Digest 365. Site investigations should be undertaken in locations and at proposed depths of the proposed infiltration devices. Proposal of the attenuation that is achieving half emptying time within 24 hours. If no ground investigations are possible or infiltration is not feasible on site, evidence of alternative surface water disposal routes (as follows) is required.
· Where surface water is connected to the public sewer, agreement in principle from United Utilities is required that there is adequate spare capacity in the existing system taking future development requirements into account. An email of acceptance of proposed flows and/or new connection will suffice.


UU requested the surface water connection on Nell Lane, to their asset to be proven. As such, a survey has been undertaken as per Condition 11, to prove where we are interfacing on the UU manhole in Nell Lane. 

On the call, the survey video was watched by all parties and the report reviewed. It was noted by UU that it looked to be satisfactory and should be sufficient to discharge the condition. See further commentary / details below.

SURFACE WATER CONNECTION – NELL LANE
· CCTV survey and report completed – no issues with connection. We surveyed from the final manhole on that line to the UU manhole in Nell Lane. It was not possible to survey along this line as it is a 1500mm line.  
· This is the existing connection that the new CDC is tapping into. 
· Only 5 liter per second is being added to the existing flow rate. 
· See attached mark up showing locations of survey 
· Note - The surface water connection has a hydrobrake / flow control on our site and there is also a flow limiter on the existing link from hospital to Nell Lane sewer. 


FOUL WATER CONNECTION – BURTON ROAD
· CCTV survey and report completed – no issues with connection. 
· This is the existing connection that the new CDC is tapping into. 
· See attached mark up showing locations of survey 
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