| Applications | Structure and Operation |
| --- | --- |
| For purification of supply air, exhaust air and circulating air streams from harmful gases, steams and bad smells in: - Canteen kitchens, museums, waste recycling centres - Hospitals, laboratories, computer areas - Chemical industry, paintshops, airports, petrol stations, parking garages | - Solid carbon - Strong robust galvanized frame - Humidity resistant up to 70% r. h. - Temperature resistant up to max. 40°C |

| Versions | Contact time (Dwell Time) |
| --- | --- |
| - V-Formation - Standard Duty - Heavy Duty - Removes hydrogen sulphide, ammonia, DMS etc. | - 0.1 Second – 0.4 Second - Please ask for recommendations on dwell time |

| Tri-carb Safe Fit | 24x8x24 | Tri-carb Safe Fit | 3 x 24x8x24 |
| --- | --- | --- | --- |
| Dimensions | 595x198x595 | Dimensions | 595x595x595 |
| Gross Weight | 22.00KG | Gross Weight | 66.00Kg |
| Carbon Weight | 17.00KG | Carbon Weight | 51KG |
| Rated Velocity | 1266 M3/h | Rated Velocity | 3800 M3/h |
| Pressure Drop SD | 185Pa | Pressure Drop SD | 185Pa |

Tri-Carb Dimensions

|  |  |  |  | ( | ( |  |
| --- | --- | --- | --- | --- | --- | --- |
| TSF180912 | 2 | 18x18x12 | 451x220x295 | 6.5 | 9.85 | 473 |
| TSF240612 | 2 | 24x12x12 | 595x146x295 | 6.5 | 8.80 | 469 |
| TSF240812 | 3 | 24x24x12 | 595x198x295 | 8.68 | 11.00 | 625 |
| TSF180918 | 2 | 18x18x18 | 451x220x451 | 10.08 | 13.85 | 725 |
| TSF240618 | 2 | 24x12x18 | 595x146x451 | 9.98 | 13.22 | 719 |
| TSF240818 | 3 | 24x24x18 | 595x198x451 | 13.31 | 16.55 | 958 |
| TSF180924 | 2 | 18x18x24 | 451x220x595 | 13.31 | 16.55 | 958 |
| TSF240624 | 2 | 24x12x24 | 595x146x595 | 13.18 | 16.68 | 950 |
| TSF240824 | 3 | 24x24x24 | 595x198x595 | 17.58 | 22.00 | 1266 |

The above capacities are based on a 0.1 second dwell time. Please refer to the table below for the recommended minimum dwell times required for different applications and scale up accordingly. It should be noted that filtration performance will be improved by increasing the dwell times applied. The appropriate suffix should be added to the part number to specify the required grade e.g.

TRI240824CU50

| General Cooking | 0.1 – 0.2 | COL-A50 | OLA-50 |
| --- | --- | --- | --- |
| Spicy – Indian | 0.2 – 0.4 | COL-A50 | OLA-50 |
| Reduction of Kerosene | 0.1 – 0.2 | COL-A50 | OLA-50 |
| Reduction of Ozone | 0.1 – 0.2 | COC-A50 | OCA-50 |
| Diesel Fumes | 0.2 | SORB17 | SORB17 |
| Museum | 0.2 | Museum Grade | CU-50 |
| Mortuary | 0.4 | Mortuary Grade | FORM |
| Ammonia | 0.3 | Ammonia Grade | AMM |

Other Applications

We can formulate gas phase filters for most applications, simply contact us with your enquiry.