## Material List
Material List
Model | Qty | Description
REYQ8U | 1 | REYQ-U (VRV IV)
REYQ10U | 2 | REYQ-U (VRV IV)
REYQ12U | 1 | REYQ-U (VRV IV)
BS6Q14AV1B | 1 | Branch selector unit
BS8Q14AV1B | 3 | Branch selector unit
FXFQ32B | 2 | FXFQ-B - Round Flow Round flow cassette
FXFQ63B | 2 | FXFQ-B - Round Flow Round flow cassette
FXSQ15A | 1 | FXSQ-A - Concealed ceiling unit with medium ESP
FXSQ40A | 9 | FXSQ-A - Concealed ceiling unit with medium ESP
FXSQ50A | 9 | FXSQ-A - Concealed ceiling unit with medium ESP
FXSQ63A | 1 | FXSQ-A - Concealed ceiling unit with medium ESP
FXZQ15A | 2 | FXZQ-A - Fully flat cassette
FXZQ20A | 1 | FXZQ-A - Fully flat cassette
DCM601A51 | 1 | Intelligent Touch Manager
DMS502A51 | 1 | BACnet Interface - integrated control system connecting VRV system with BMS system
BRC1H52W | 13 | Remote controller (white)
BYCQ140E | 4 | Standard decoration panel
BYFQ60CW | 3 | New decoration panel (white)
R410A | 0.0kg | Extra refrigerant charge
Refrigerant Piping
Pipe Size | Total Length | Number of Bends
1/4 | 0.0 | 0
3/8 | 0.0 | 0
1/2 | 0.0 | 0
5/8 | 0.0 | 0
3/4 | 0.0 | 0
7/8 | 0.0 | 0
1 1/8 | 0.0 | 0

## Schedules-IDU
VARIABLE REFRIGERANT VOLUME - INDOOR UNIT SCHEDULE
TAG | ROOM | BASIS OF DESIGN (DAIKIN) | NOMINAL CAPACITY | TYPE | CONNECTED TO: |  | SUPPLY FAN | COOLING CAPACITY |  |  |  | HEATING CAPACITY |  | ELECTRICAL |  |  | DIMENSIONS | WEIGHT | NOTES | Options and Accessories
[5 empty] | CONDENSING UNIT | ZONE CHANGEOVER DEVICE | AIR FLOW RATE l/s | TOTAL kW | SENSIBLE kW | ENTERING AIR |  | TOTAL kW | ENTERING AIR °Cdb | POWER SUPPLY | Min Circuit Amps | Max Overcurrent Protection | WxHxD | Net
[10 empty] | °C DB | °C WB |  |  | Voltage - Phase | MCA | MOP | mm | kg
FCU/00/01 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 1 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5 |  | BRC1H52W (1)
FCU/00/05 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 1 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5
FCU/00/06 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 1 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5
FCU/00/09 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 1 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5
FCU/00/11 | Stock Room | FXFQ32B | 3 | Round Flow Round flow cassette | Level 0 - System 1 | Yes | 213.33 | 3.0 | 2.6 | 23.0 | 16.2 | 3.9 | 21.0 | 220V 1ph | 0.3 | 16.0 | 840 x 204 x 840 | 18.0 |  | BRC1H52W (1), BYCQ140E (1)
BS/GF/02 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 2 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5 |  | BRC1H52W (1)
BS/GF/03 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 2 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5
BS/GF/04 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 2 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5
BS/GF/07 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 2 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5
BS/GF/08 | Front of House | FXSQ40A | 4 | Concealed ceiling unit with medium ESP | Level 0 - System 2 | Yes | 250.00 | 3.7 | 2.9 | 23.0 | 16.2 | 4.8 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 28.5
BS/GF/10 | Changing | FXSQ15A | 2 | Concealed ceiling unit with medium ESP | Level 0 - System 2 | Yes | 145.00 | 1.4 | 1.1 | 23.0 | 16.2 | 1.8 | 21.0 | 220V 1ph | 0.8 | 16.0 | 550 x 245 x 800 | 23.5 |  | BRC1H52W (1)
BS/GF/12 | Stock Room | FXFQ32B | 3 | Round Flow Round flow cassette | Level 0 - System 2 | Yes | 213.33 | 3.0 | 2.6 | 23.0 | 16.2 | 3.9 | 21.0 | 220V 1ph | 0.3 | 16.0 | 840 x 204 x 840 | 18.0 |  | BRC1H52W (1), BYCQ140E (1)
FCU/01/01 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 3 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0 |  | BRC1H52W (1)
FCU/01/03 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 3 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0
FCU/01/04 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 3 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0
FCU/01/07 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 3 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0
FCU/01/08 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 3 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0
FCU/01/10 | Changing | FXSQ63A | 6 | Concealed ceiling unit with medium ESP | Level 1 - System 3 | Yes | 350.00 | 5.8 | 4.5 | 23.0 | 16.2 | 7.7 | 21.0 | 220V 1ph | 1.6 | 16.0 | 1,000 x 245 x 800 | 35.5 |  | BRC1H52W (1)
FCU/01/12 | One 2 One | FXZQ15A | 2 | Fully flat cassette | Level 1 - System 3 | Yes | 141.67 | 1.4 | 1.3 | 23.0 | 16.2 | 1.8 | 21.0 | 220V 1ph | 0.3 | 16.0 | 575 x 260 x 575 | 15.5 |  | BRC1H52W (1), BYFQ60CW (1)
FCU/01/15 | Stock Room | FXFQ63B | 6 | Round Flow Round flow cassette | Level 1 - System 3 | Yes | 276.67 | 5.8 | 4.5 | 23.0 | 16.2 | 7.7 | 21.0 | 220V 1ph | 0.4 | 16.0 | 840 x 204 x 840 | 21.0 |  | BRC1H52W (1), BYCQ140E (1)
FCU/01/02 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 4 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0 |  | BRC1H52W (1)
FCU/01/05 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 4 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0
FCU/01/06 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 4 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0
FCU/01/09 | Front of House | FXSQ50A | 5 | Concealed ceiling unit with medium ESP | Level 1 - System 4 | Yes | 253.33 | 4.6 | 3.6 | 23.0 | 16.2 | 6.1 | 21.0 | 220V 1ph | 1.1 | 16.0 | 700 x 245 x 800 | 29.0
FCU/01/11 | Office | FXZQ15A | 2 | Fully flat cassette | Level 1 - System 4 | Yes | 141.67 | 1.4 | 1.3 | 23.0 | 16.2 | 1.8 | 21.0 | 220V 1ph | 0.3 | 16.0 | 575 x 260 x 575 | 15.5 |  | BRC1H52W (1), BYFQ60CW (1)
FCU/01/13 | Break | FXZQ20A | 2 | Fully flat cassette | Level 1 - System 4 | Yes | 145.00 | 1.8 | 1.5 | 23.0 | 16.2 | 2.4 | 21.0 | 220V 1ph | 0.3 | 16.0 | 575 x 260 x 575 | 15.5 |  | BRC1H52W (1), BYFQ60CW (1)
FCU/01/14 | Stock Room | FXFQ63B | 6 | Round Flow Round flow cassette | Level 1 - System 4 | Yes | 276.67 | 5.8 | 4.5 | 23.0 | 16.2 | 7.7 | 21.0 | 220V 1ph | 0.4 | 16.0 | 840 x 204 x 840 | 21.0 |  | BRC1H52W (1), BYCQ140E (1)

## Schedules-ODU-AIR
VARIABLE REFRIGERANT VOLUME - AIR-COOLED CONDENSING UNIT SCHEDULE
TAG: ROOM | BASIS OF DESIGN (DAIKIN) | NOMINAL CAPACITY | DESCRIPTION | COOLING CAPACITY |  | HEATING CAPACITY |  | REFRIGERANT CHARGE |  | CONNECTION RATIO (%) | ELECTRICAL | [12 empty] | DIMENSIONS |  | NOTES | Options and Accessories
[11 empty] | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) |  |  |  | MAX OVERCURRENT PROTECTION (MOP) |  |  |  | RUNNING CURRENT(RLA)
|  |  |  | kW | AMBIENT DESIGN (°C DB) | kW | AMBIENT DESIGN (°C DB / WB) | Factory Charge (kg) | Add'l Refrigerant (kg) |  |  | mod #1 | mod #2 | mod #3 | total | mod #1 | mod #2 | mod #3 | total | mod #1 | mod #2 | mod #3 | total | (WxHxD) (mm) | WEIGHT (kg)
Level 0 - System 1 | REYQ8U | 8 | Air cooled heat recovery (1) | 15.1 | 35.0 | 18.6 | -5.0 / -5.0 | 9.7 | n/a | 95.6 | 400V 3Nph | 16.1 |  |  | 16.1 | 20 |  |  | 20 | 7.7 |  |  | 7.7 | 930 x 1,685 x 765 | 230.0
Level 0 - System 2 | REYQ10U | 10 | Air cooled heat recovery (1) | 19.0 | 35.0 | 21.0 | -5.0 / -5.0 | 9.8 | n/a | 98.5 | 400V 3Nph | 22 |  |  | 22 | 25 |  |  | 25 | 10.5 |  |  | 10.5 | 930 x 1,685 x 765 | 230.0
Level 1 - System 3 | REYQ12U | 12 | Air cooled heat recovery (1) | 29.8 | 35.0 | 25.4 | -5.0 / -5.0 | 9.9 | n/a | 130.0 | 400V 3Nph | 24 |  |  | 24 | 32 |  |  | 32 | 13.8 |  |  | 13.8 | 930 x 1,685 x 765 | 230.0
Level 1 - System 4 | REYQ10U | 10 | Air cooled heat recovery (1) | 22.9 | 35.0 | 22.5 | -5.0 / -5.0 | 9.8 | n/a | 119.0 | 400V 3Nph | 22 |  |  | 22 | 25 |  |  | 25 | 10.5 |  |  | 10.5 | 930 x 1,685 x 765 | 230.0

## Schedules-HR BOX
VARIABLE REFRIGERANT VOLUME - ZONE HEAT RECOVERY DEVICE SCHEDULE
TAG: ROOM | BASIS OF DESIGN (DAIKIN) | CONDENSING UNIT SERVED | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) | MAX OVERCURRENT PROTECTION (MOP) | MAX CAPACITY (per Port) | DIMENSIONS (WxHxD mm) | WEIGHT (kg) | ZONE SERVED | Options and Accessories
BS/GF/01 | BS6Q14AV1B | Level 0 - System 1 | 230V 1ph | 0.6 | 15.0 | 41.0 | 580 x 298 x 430 | 28.0
BS/GF/02 | BS8Q14AV1B | Level 0 - System 2 | 230V 1ph | 0.8 | 15.0 | 41.0 | 580 x 298 x 430 | 31.0
BS/01/01 | BS8Q14AV1B | Level 1 - System 3 | 230V 1ph | 0.8 | 15.0 | 41.0 | 580 x 298 x 430 | 31.0
BS/01/02 | BS8Q14AV1B | Level 1 - System 4 | 230V 1ph | 0.8 | 15.0 | 41.0 | 580 x 298 x 430 | 31.0