
3.0   EMAQ report and RA


A site survey was carried out on 5th April  2023, and all items on the EMAQ risk assessment form were investigated and assessed.



Pizza Oven Extract
Dispersion will be at low level (3.0m afl)  wall louvre, so scores 20

Proximity of Receptors was assessed to be between  20m and 100m,   receptors are mainly  commercial, it was subsequently scored 5

Size of Kitchen  falls into the small size of kitchen, less than 30 covers, so scores 1

Cooking type is pizza etc, so was scored 4



Total Score is 30 which falls into the ‘high level’ of odour control, so odour control equipment comprising a Purified Air MFU Multi Filtration Unit has been selected




