Wastewater Developer Services Engineer Feedback Form (S185)

Proposed Section 185 Diversion at Plot 10a, First Street, Manchester UU Reference – 03032983

|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date of UU response | 09/03/2023 | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. |

Form contents

| Section 1 – Information required for a Section 185 submission | Section 2 – Initial check of the high level strategy |
| --- | --- |
| Section 3 – CCTv surveys / Sewer Abandonment 3a CCTv surveys 3b Abandonment plan | Section 4 – Drawings checklist / Technical Appraisal comments 4a S185 Agreement Plan 4b Land registry compliant plan 4c Long sections 4d Manhole schedules / 1:20 details 4e Other drawings (delete if applicable) |

# Section 1 - Information required for Section 185 submission

Note: any item selected as ‘not submitted’ will need to be provided to support and progress the application to Technical Acceptance.

Please note that United Utilities Developer Services support guide is available to download from our webpage using the following link:

This shows how information should be provided for a variety of technical plans and also highlights critical design checks that need to be satisfied.

| Section 1 Information required | Submitted | Not submitted | N/A | Designer Tick to highlight where information noted as ‘not submitted’ has now been provided |
| --- | --- | --- | --- | --- |
| - S185 agreement plan | ☒ | ☐ | ☐ | ☐ |
| - Long section drawings | ☒ | ☐ | ☐ | ☐ |
| - Manhole schedules / 1:20 details In certain circumstances, it can make sense for the overall strategy to be checked for compliance in principal before the manhole schedules / 1:20 details are drawn up. However please note that manhole sizes will not be confirmed or accepted until formal technical acceptance is given (the scaled layout can show the need to adjust manhole diameters) | ☒ | ☐ | ☐ | ☐ |
| - A3 land registry compliant plan A PDF copy of a plan with full extent of land edged green shown, scale as near to 1:1250 or 1:500 as possible at A3 size, North Arrow, Landmarks and road names, Easement strip dimensioned and coloured yellow (if there are any). The green boundary should be closed so that the ‘parcel’ of land is identifiable and the development needs to fit the whole page. | ☒ | ☐ | ☐ | ☐ |
| - Abandonment plan (if applicable) | ☒ | ☐ | ☐ | ☐ |
| - CCTV survey (if applicable) - A copy of the report and CCTV footage is to be provided. The numbering of survey lengths should correspond with the drainage layout. | ☒ | ☐ | ☐ | ☐ |
| - Local council planning consent | ☐ | ☒ | ☐ | ☐ |
| - Copy of the site investigation report & (remediation strategy – if applicable) | ☐ | ☒ | ☐ | ☐ |
| - Topographical Survey | ☒ | ☐ | ☐ | ☐ |

# Section 2 – Initial check of the high level strategy

| High level check |  |  |  | Yes | No | TBC | See comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - Is the proposed diversion shown to be within the Development boundary? |  |  |  | ☐ | ☐ | ☒ | ☒ |
| - Has permission been given for the diversion to be carried out by the developer? |  |  |  | ☐ | ☐ | ☐ | ☒ |
| - Does the proposed design give United Utilities a cost effective proposal for the life of the assets, considering the long term operability? |  |  |  | ☐ | ☐ | ☒ | ☒ |
| - Are the proposed gradients and proposed routing of the diverted sewers acceptable? |  |  |  | ☐ | ☐ | ☒ | ☒ |
| - Does the proposal show any cover levels on the proposed diverted sewer to be lower than the existing public sewer cover levels/ nearby cover levels? In the absence of modelling information of the existing sewer, we do not recommend that any manhole cover levels are lowered as part of the proposed works. |  |  |  | ☐ | ☒ | ☐ | ☐ |
| - Has the line, level, position and diameter of the existing sewers been verified at the proposed points of connection? |  |  |  | ☐ | ☐ | ☒ | ☒ |
| Date | Comment number | Engineer General comments | Designers comments | Status (To be completed by UU personnel only) |  |  |  |
| 09/03/2023 | 1 | Please advise if the shown greenline boundary is public highway (River Street) or is River Street within the landowners boundary? One of the conditions that need to be met to self lay the diverted sewer is: 1) The developer owns all the land where the diversion is taking place. | River Street is currently within the footprint of First Street Development Ltd. And will remain under their ownership. Therefore, River Street is not currently within public highway, there is of course the possibility that this may change in the future. However, at the time of making this application the above is believed to be correct. The site is owned by the First Street Development Ltd | Action required |  |  |  |
| 09/03/2023 | 2 | Has permission been given for the diversion to be carried out by the developer? | The developer is the applicant and landowner, and hence has confirmed they wish to divert the sewer, relocating it from one part of their land to another. Through discussions with UU, dating back several years, UU have advised that in principle they consider the proposed diversion to be acceptable (subject to technical review). The developer proposes to undertake the diversion works, rather than request that UU to undertake the diversion works, and the developer understand that the contractor will need to be approved by UU to undertake the diversion works. | Action required |  |  |  |
| 09/03/2023 | 3 | Has the line, level, position and diameter of the existing sewers been verified at the proposed points of connection? | Yes, by survey where access was available. | Action required |  |  |  |
| 09/03/2023 | 4 | - Please provide correspondence from the gas main utility company to understand if the overlapping of United Utilities required sewer easement can be located within the gas main easement and if this would be acceptable. - Please advise if the low pressure gas main has an easement and if laying the sewer as proposed is acceptable with the gas utility company. - The existing 125mm gas main running near proposed MH CS06 has not been accurately located and as such may be being built over, will you locate this asset accurately before works are carried out? and discuss and provide correspondence from Cadent on their required easement and their acceptance on building a new manhole near to the main after it is accurately located. It may be practical to adjust the location of the manhole towards the kerb away from the mapped line of the gas main. - Please provide correspondence from Cadent confirming the gas main within the route of the proposed diverted sewer can be abandoned. - Please provide RAMS/further information for measures on future access (excavation) to the proposed diverted sewer running adjacent to existing gas mains and how this can be safely carried out where the existing services are within our easement. | We have developed the drainage diversion proposals in parallel with discussions with Cadent. We have requested a formal response from Cadent confirming acceptance of each of the points you have raised, and will issue to you as soon as this is received. | Action required |  |  |  |
| 09/03/2023 | 5 | Please include the proposed building/foundation outlines on the plans and provide a section drawing to understand if there will be any loading on the sewer from the buildings as per DCG document figure B1 if the required easement is not met. | Sections added to cross sections drawing RAM-XX-XX-DR-D-10255 | Action required |  |  |  |
| 09/03/2023 | 6 | Please include cover and invert levels for the proposed diverted sewer on the diversion plan. | Cover & invert levels now shown on diversion plan (RAM-XX-XX-DR-D-10100) | Action required |  |  |  |

| Other general comments |  |  |  | Yes | No | TBC | N/A | See comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| If applicable, has ground remediation been considered at the depths and location of the proposed sewers offered for adoption? |  |  |  | ☐ | ☐ | ☒ | ☐ | ☒ |
| Has 0.5m clearance been achieved from kerb line to outer ring wall of manholes and 1.0m clearance to outer wall of sewers included in the diversion proposals? |  |  |  | ☐ | ☒ | ☐ | ☐ | ☒ |
| Has a minimum 300mm clearance been achieved between pipe crossings? Please note that this distance must be between the outer walls of pipes |  |  |  | ☐ | ☐ | ☒ | ☐ | ☒ |
| Are there any walls higher than 1.8m or any retaining walls within the development in proximity to the diverted network that require consideration (i.e. loading) |  |  |  | ☐ | ☐ | ☒ | ☐ | ☒ |
| Confirm if any large diameter thermoplastic pipes are proposed as there will be additional information / assessment required |  |  |  | ☐ | ☐ | ☐ | ☒ | ☒ |
| Date | Comment number | Engineer comments | Designers comments |  |  |  |  | Status (To be completed by UU personnel only) |
| 09/03/2023 | 1 | If applicable, has ground remediation been considered at the depths and location of the proposed sewers offered for adoption if so please provide details | No ground remediation is required |  |  |  |  | Action required |
| 09/03/2023 | 2 | Noted that chambers are located adjacent to the kerb due to the live gas main location. | Correct, position of manhole has been discussed and agreed during the meeting with on 08/03/2023 with UU (Shoaib Tauqeer and Joanne Hill). |  |  |  |  | Action required |
| 09/03/2023 | 3 | Please advise where the proposed diversion crosses the existing private surface water sewer that 300mm clearance is achieved with the proposed diverted sewer. | Surface water network is at road level, so there is approximately 4m clearance from crossing at the points between CS02 into CS03. |  |  |  |  | Action required |
| 09/03/2023 | 4 | Has the existing private surface water sewer been accurately located- the proposed diversion runs in parallel and may clash with the proposed manholes or sewer – please accurately locate and show offset on a section plan for further assessment. (after our meeting it is understood this is kerb drainage only – please confirm) | Private sewer is at road level (via a kerb drain) so has been accurately located during survey works, will be added to section plan to show clearance. |  |  |  |  | Action required |
| 09/03/2023 | 5 | Please confirm if there are any walls to be installed over the sewer | None proposed |  |  |  |  | Action required |
| 09/03/2023 | 6 | The 150mm sewer from CS01 to CS03 does not form part of the S185 diversion and should be coloured grey. This sewer would need to be submitted as part of an S104 adoption application. | CS01 to CS03 removed from the application and replaced with a stub. Connection will be part of an S104 application in the future. |  |  |  |  | Action required |

# Section 3 – CCTv survey / sewer abandonment

| CCTv surveys / Sewer abandonment ☐ Submitted ☐ Not yet submitted |  |  |  | Yes | No | See comments |
| --- | --- | --- | --- | --- | --- | --- |
| The provided camera survey (report and disc) is acceptable and complies with the guidance available on United Utilities website? |  |  |  | ☐ | ☐ | ☒ |
| A camera survey has been provided for all affected lengths to be diverted to confirm/ disprove connectivity? |  |  |  | ☐ | ☐ | ☒ |
| Adequate investigation and or justification to confirm any observed connections are ‘dead’? This should not be assumed – all observed connections should be dye tested and traced, with drawings provided to confirm findings. |  |  |  | ☐ | ☐ | ☒ |
| Date | Comment number | Engineer comments | Designers comments | Status (To be completed by UU personnel only) |  |  |
| 09/03/2023 | 1 | Please provide CCTV footage | CCTV footage has been provided. | Action required |  |  |
| 09/03/2023 | 2 | The shown 150mm lateral incoming connections would need to be surveyed to confirm as ‘dead’ connections. It is noted that a separate document showing evidence of historic demolished housing in this area has been provided to show what these connections may have previously likely served. Please also add the below note within the drawings using a clear text box (and not in the notes section): - Any live connections are to be reconnected to the pubic sewer - UU Inspector to be present for all diversion and abandonment works - Existing sewers to be grubbed up | During the meeting with on 08/03/2023 with UU (Shoaib Tauqeer and Joanne Hill), UU advised that through engineering judgement, based on the evidence provided to date, it would be reasonable to assume the existing public sewer within Hulme Street (to the west of Wilmott Street) only collects highway drainage from Hulme Street, and no further survey work is required to prove otherwise Notes added to drawing RAM-XX-XX-DR-D-10010 | Action required |  |  |
| Click here to enter a date. |  |  |  | Choose an item. |  |  |
| Click here to enter a date. |  |  |  | Choose an item. |  |  |
| Click here to enter a date. |  |  |  | Choose an item. |  |  |

| Abandonment plan ☐ Submitted ☐ Not yet submitted | Yes (Acceptable) | No | TBC | N/A | (Designer) Tick to confirm addressed with resubmission |
| --- | --- | --- | --- | --- | --- |
| - The sewers and manholes which the developer is applying to abandon are clearly labelled and referenced with details of the pipe diameters, pipe material and also include survey numbers | ☒ | ☐ | ☐ | ☐ | ☐ |
| - The sewers which are being considered for abandonment shall be identified by using black crosses with notes confirming details of the proposed method of abandonment, e.g. grubbing out, or grouting | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Information detailed to confirm it is understood all abandonments must be witnessed for the status of the pipe to be changed on the public sewer records, confirming that the minimum of 72 hours’ notice will be provided. | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Detail of how any manholes will be abandoned should also be included on the drawing with separate sections or details to support where required | ☐ | ☐ | ☐ | ☒ | ☐ |
| - Drawing shows the position and levels of proposed sewers and manholes | ☐ | ☒ | ☐ | ☐ | ☒ |

| Date | Comment number | Engineer comments | Designers comments | Status |
| --- | --- | --- | --- | --- |
| 09/03/2023 | 1 | Please confirm/provide the requirement as stated on the 3rd point above | Yes, we confirm we will provide UU 72 hours notice for undertaking witnessing. | Action required |
| 09/03/2023 | 2 | Please add position and levels of proposed sewers and manholes on the abandonment plan | Added to drawing RAM-XX-XX-DR-D-10010 | Action required |
| 09/03/2023 | 3 | Remove other coloured utilities from the abandonment plan | Utilities removed from RAM-XX-XX-DR-D-10010 | Action required |
| Click here to enter a date. |  |  |  | Choose an item. |
| Click here to enter a date. |  |  |  | Choose an item. |
| Click here to enter a date. |  |  |  | Choose an item. |
| Click here to enter a date. |  |  |  | Choose an item. |

# Section 4 – Drawings checklists / Technical Appraisal comments

Note: any points marked as ‘No’ or ‘TBC’ will require amendments to the drawings.

The Engineer will make comments in the column named ‘Engineers comments’. Should these comments ask questions please ensure that you provide response comments (with clarification and or justification) in the adjacent column.

Note: Designer’s response comments must be given to any Engineer comments for the application to progress to Technical Acceptance.

| Section 4a ## S185 Agreement Plan ☐ Submitted ☐ Not yet submitted | Yes (Acceptable) | No | TBC | N/A | (Designer) Tick to confirm addressed with resubmission |
| --- | --- | --- | --- | --- | --- |
| - Boundary shown in green (and clearly visible). The green boundary must surround all of the works including any 3rd party land owners. Landmarks and road names will also be required. If this cannot be shown on one drawing then a separate location plan must be provided to show the full extent of the development boundary again, including landmarks and road names so the site can be easily identified | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Scaled to fit A1 or A0 | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Sewers proposed for diversion to be coloured as follows; (foul – brown, combined – red, surface water – blue) | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Any sewers proposed for abandonment are shown in a black cross hatched line | ☐ |  | ☒ |  | X |
| - Existing sewers, highway drains, culverted watercourses shown in black (not coloured) | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Easements – - Coloured yellow and dimensioned? – see UU easement local practice | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Provided where sewer runs through third party land? | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Provided for a surface water outfall pipe to watercourse? | ☐ | ☐ | ☐ | ☒ | ☐ |
| - Pipe lengths labelled with the diameter, gradient and pipe material | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Manholes labelled with cover and invert levels | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Finished floor levels shown for the plots | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Road numbering system clearly visible | ☒ | ☐ | ☐ | ☐ | ☐ |

| Drawing number: RAM-XX-XX-DR-C-101 | Revision | P07 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Date | 28/02/2023 | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. |

| Rev. | Comment number. | Engineers comments | Designer’s response comments | Status |
| --- | --- | --- | --- | --- |
|  | 1 | Please amend the boundary plan after removing CS01 and the sewer running to CS03 | Drawing RAM-XX-XX-DR-D-10100 amended to suit layout. | Action required |
|  | 2 | Please provide details on all the proposed plot developments to connect into this sewer which is to be diverted including detailed drainage design for each plot, proposed surface and foul water discharge rates, finished floor levels and information on any proposed basements. | Information added to drawings, however for clarity. Flow from various sites: Plot 9a: Foul 3.2 l/s, Surface 7.5 l/s Plot 10a: Foul 5.9 l/s, Surface 5 l/s Plot 10b: Foul 4.8 l/s, Surface 4.9 l/s Total flow rate: 31.3 l/s Plot 9a drainage drawing attached. Plot 10a & 10b are currently at Stage 3. Flow rates will not be exceeded. FFL & basement information: Plot 9a: GF 30.940 Basement: 27.240 Plot 10a: GF 30.930 Basement: 29.005 Plot 10b: GF 30.925 No Basement | Action required |
|  | 3 | Grey out all utilities/private assets shown apart from UU assets part of the S185. The redline boundary should also be removed. | Drawing RAM-XX-XX-DR-D-10100 amended to suit comment. | Action required |
|  | 4 | Please show section of sewer to be abandoned | Drawing RAM-XX-XX-DR-D-10100 amended to suit comment. | Action required |
|  | 5 | Amend the shown easements in line with United Utilities easement local practice guidance for new sewers. https://www.unitedutilities.com/builders-developers/wastewater-services/sewer-adoptions/adopt-a-sewer/ | Drawing RAM-XX-XX-DR-D-10100 amended to suit comment. | Action required |
|  | 6 | Please label manholes on the diversion plan with cover and invert level information | Drawing RAM-XX-XX-DR-D-10100 amended to suit comment. | Action required |
|  | 7 | Please provide information to understand if self cleansing velocity will be achieved for the diverted sewer | Information provided within correspondence on 13/03/2023 which confirms self-cleansing velocity will be achieved. | Action required |

| Section 4b A3 Land registry plan ☐ Submitted ☐ Not yet submitted | Yes (Acceptable) | No | TBC | N/A | (Designer) Tick to confirm addressed with resubmission |
| --- | --- | --- | --- | --- | --- |
| - A PDF copy of a plan scale as near to 1:1250 as possible at A3 size (or a suitable scale for UU legal) | ☒ | ☐ | ☐ | ☐ | ☐ |
| - North Arrow, Landmarks, coordinates and a minimum of two road names clearly visible | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Outline of the plots visible | ☐ | ☒ | ☐ | ☐ | ☒ |
| - Site boundary shows the full extent of the land edged green. (This green boundary should be closed so that the ‘parcel’ of land is identifiable) | ☐ | ☒ | ☐ | ☐ | ☒ |
| - Easement strip coloured yellow and dimensioned? – see UU easement local practice | ☐ | ☒ | ☐ | ☐ | ☒ |
| - Sewers proposed for diversion to be coloured as follows; (foul – brown, combined – red, surface water – blue) | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Ensure the words ‘DO NOT SCALE’ are not contained within the drawing | ☒ | ☐ | ☐ | ☐ | ☐ |

| Drawing number: RAM-XX-XX-DR-C-100 | Revision | P05 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Date | 28/02/2023 | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. |

| Rev. | Comment number. | Engineers comments | Designer’s response comments | Status |
| --- | --- | --- | --- | --- |
|  | 1 | Remove gas main easement, and remove redline, add a green line boundary to include the development land as well as the area of S185 diversion works | Items removed & green line boundary extended to include development land on RAM-XX-XX-DR-D-10001 | Action required |
|  | 2 | Amend easement width on plan to suit UU local practice easement guide. | Easement amended on drawings RAM-XX-XX-DR-D-10001 & RAM-XX-XX-DR-D-10100 | Action required |
|  |  |  |  | Choose an item. |
|  |  |  |  | Choose an item. |
|  |  |  |  | Choose an item. |
|  |  |  |  | Choose an item. |

For comments made within Section 4c, long sections and 4d – Manhole Schedules/1:20 details, changes are to be made as requested, the designer response comments section should only be used if the requested changes are not feasible. In such instances, sufficient justification should be provided.

Please ensure that anything ticked as ‘no’ or ‘TBC’ within the check list has been addressed on all drawings provided with your resubmission.

| Section 4c ## Long sections ☐ Submitted ☐ Not yet submitted | Yes (Acceptable) | No | TBC | N/A | (Designer) Tick to confirm addressed with resubmission |
| --- | --- | --- | --- | --- | --- |
| - Connections to the public sewer are shown to be made at soffit to soffit level | ☐ | ☐ | ☐ | ☐ | ☐ |
| - Manholes labelled with the cover and invert levels | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Pipe lengths are labelled with pipe diameters, numbers, materials and gradients | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Pipe bedding detail confirmed for each pipe length | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Adequate cover is provided to the pipes and that concrete protection is indicated where necessary (this can be via pipe surround or slab | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Proposed gradients are appropriate | ☒ | ☐ | ☐ | ☐ | ☐ |
| - The existing and proposed ground levels are shown, with the chainage (linear distance) | ☐ | ☒ | ☐ | ☐ | ☐ |
| - Pipe crossings are shown to confirm acceptable vertical clearance - Additionally the relative location of other known service crossings shown | ☐ | ☐ | ☒ | ☐ | ☐ |

| Drawing number: RAM-XX-XX-DR-C-10250 | Revision | P04 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Date | 28/02/2023 | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. |

| Rev. | Comment number. | Engineers comments | Designer’s response comments | Status |
| --- | --- | --- | --- | --- |
|  | 1 | Please show existing ground level | No changes are proposed to existing ground level. However, existing ground level spot levels provided across long sections drawing RAM-XX-XX-DR-D-10250 | Action required |
|  | 2 | Please show existing private surface water crossing if applicable | Existing crossing from kerb drain added on drawing RAM-XX-XX-DR-D-10250 | Action required |
|  | 3 | Please remove 150mm pipe as it is not part of the S185 | 150mm pipe removed from all drawings. Comment noted regarding future connection on drawing RAM-XX-XX-DR-D-10250 | Action required |
|  | 4 | Provide long section for the existing sewer | Long section provided for existing sewer on drawing RAM-XX-XX-DR-D-10250 | Action required |
|  |  |  |  | Choose an item. |

| Section 4d Manhole schedules / 1:20 details ☐ Submitted ☐ Not yet submitted | Yes (Acceptable) | No | TBC | N/A | (Designer) Tick to confirm addressed with resubmission |
| --- | --- | --- | --- | --- | --- |
| - Manholes referenced and correspond with the drainage layout | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Manholes labelled with the cover and invert levels | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Depth to soffit displayed (depth to cut out landing for shallow manholes and depth to invert for flow control manholes) | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Check to confirm no manholes >6m depth (For any manholes identified this should be designed out where possible and if unavoidable a bespoke design must be supplied with an intermediate landing). | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Manhole diameter noted | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Manhole type noted (as per UU Standard Construction Details or Design & Construction Guidance) | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Minimum benching widths dimensioned and achieved | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Direction of flow shown | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Hole size in cover slab noted for each manhole | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Drawings confirm that all lateral connections will be made at soffit level to the main channel | ☐ | ☐ | ☒ | ☐ | ☒ |
| - Use of appropriate rocker pipe lengths confirmed/ reference to variable features on STND/19/010 | ☒ | ☐ | ☐ | ☐ | ☐ |
| - Detail provided for any connections proposed to an existing manhole A detail must be provided to confirm feasibility and ensure there is adequate space to facilitate the additional connection. Where a connection will cause detriment, for example passing through the landing space, a detail should show how this will be upgraded to suit the new connection. | ☐ | ☐ | ☐ | ☒ | ☐ |

| Drawing number: RAM-XX-XX-DR-C-10 | Revision | P05 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Date | 28/02/2023 | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. | Click here to enter a date. |

| Rev. | Comment number. | Engineers comments | Designer’s response comments | Status |
| --- | --- | --- | --- | --- |
|  | 1 | Please ensure anything with the tick box selected with ‘no’ or ‘TBC’ is addressed on the revised drawing | All items added to drawing RAM-XX-XX-DR-D-10200 | Action required |
|  | 2 | Please revise the manholes schedules and plans in line with the requirements for a 600mm diameter sewer. The manhole schedules and plans require updating to suit a 600mm sewer i.e. required benching width etc. | Manholes with additional requirements for 600mm pipework amended to suit guidance on drawing RAM-XX-XX-DR-D-10200 | Action required |
|  | 3 | Please add a note that all lateral connections will be made at soffit level to the main channel | Note added regarding lateral connections on drawing RAM-XX-XX-DR-D-10200 | Action required |
|  |  |  |  | Choose an item. |