## Front Cover
Issue Status: | TENDER ISSUE
Document Ref: | 27618-979000
Date of Issue: | 2022-04-29
Revision: (see next page for details) | P01
Author: | ROB FRANCIS
Checked By: | BARRY TURPIN
Approved By: | SIMON RAMSDEN
Copyright  HILSON MORAN – 2020 All rights reserved. This Technical Specification has been produced by Hilson Moran Partnership Ltd. No part of this document may be reproduced in any material form without the written permission of a Director of Hilson Moran Partnership Ltd. Enquiries about copyright should be made to the Technical Director at the Hilson Moran Partnership Ltd offices in London.
TECHNICAL SCHEDULES
FOR THE
ELECTRICAL SERVICES
SCHEDULE OF LIGHTING & POWER
DISTRIBUTION BOARDS

## Revision History
SCHEDULE REVISION HISTORY
Rev. | Date | Schedule | Details
P01 | 29.4.2022 | ALL | TENDER ISSUE

## E979000
E979000 | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: | 27618
REVISION: | P01
PROJECT NAME: | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF:
INDEX
SCHEDULE | BOARD REFERENCE | TYPE | LOCATION
E979001 | Main Switchboard MSB | 19 WAY TP&N | Basement LV Switchroom
E979002 | DB LB-MS | 6 WAY TP&N | Basement LV Switchroom
E979003 | DB LB-GLP | 8/8 WAY TP&N | Basement South Electrical Riser
E979004 | DB LG-GLPS | 8/8 WAY TP&N | Ground Floor South Electrical Riser
E979005 | DB LG-GLPN | 8/8 WAY TP&N | Ground Floor North Electrical Riser
E979006 | DB TG02-GLPS | 8/8 WAY TP&N | Ground Floor Tenant G02
E979007 | DB TF03-GLPS | 8/8 WAY TP&N | 1st Floor South Electrical Riser
E979008 | DB TS04-GLPS | 8/8 WAY TP&N | 2nd Floor South Electrical Riser
E979009 | DB TS05-GLPN | 8/8 WAY TP&N | 2nd Floor North Electrical Riser
E979010 | DB TT06-GLPS | 8/8 WAY TP&N | 3rd Floor South Electrical Riser
E979011 | DB TT07-GLPN | 8/8 WAY TP&N | 3rd Floor North Electrical Riser
E979012 | DB LR-GLP | 18/4 WAY TP&N | Roof Level Plantroom
E979013 | DB LB-MSS | 10 WAY SP&N | Basement South Electrical Riser
E979014 | DB LG-MSS | 4 WAY TP&N | Ground Floor South Electrical Riser
E979015 | DB TG02-MSS | 10 WAY SP&N | Ground Floor Tenant G02
E979016 | DB TF03-MSS | 10 WAY SP&N | 1st Floor South Electrical Riser
E979017 | DB TS04-MSS | 10 WAY SP&N | 2nd Floor South Electrical Riser
E979018 | DB TS05-MSN | 10 WAY SP&N | 2nd Floor North Electrical Riser
E979019 | DB TT06-MSS | 10 WAY SP&N | 3rd Floor South Electrical Riser
E979020 | DB TT07-MSN | 10 WAY SP&N | 3rd Floor North Electrical Riser
E979021 | DB LB-Mist | 10 WAY SP&N | 57 Spring Gardens Basement
E979022 | DB LR-MS | ?? WAY TP&N | Roof Level Plantroom
E979023 | DB TG01-MPB | ?? WAY TP&N | Basement North Electrical Riser
E979024 | DB TG01-GLP1 | ?? WAY TP&N | Basement North Electrical Riser
E979025 | DB TG01-GLP2 | ?? WAY TP&N | Ground Floor North Electrical Riser
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979001 (MSB)
E979001 |  |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | Main Switchboard MSB
BOARD TYPE: |  |  | 800A Fuseboard (Form 3b, Type 2, IP31, 36kA 1s)
INCOMING DEVICE: |  |  | 800A MCCB
SUPPLY ORIGIN: |  |  | 57 Spring Gardens Main Switchboard
PROTECTIVE DEVICE: |  |  | 630A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Basement LV Switchroom
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
L1
1 | L2
L3
L1
2 | L2
L3
L1
3 | L2
L3
L1
4 | L2
L3
L1
5 | L2
L3
L1
6 | L2
L3
L1
7 | L2
L3
L1
8 | L2
L3
L1
9 | L2
L3
L1
10 | L2
L3
L1
11 | L2
L3
L1
12 | L2
L3
L1
13 | L2
L3
L1
14 | L2
L3
L1
15 | L2
L3
L1
16 | L2
L3
L1
17 | L2
L3
L1
18 | L2
L3
L1
19 | L2
L3
| L1 | Blank
20 | L2 | Blank
| L3 | Blank
| L1 | Blank
21 | L2 | Blank
| L3 | Blank
| L1 | Blank
22 | L2 | Blank
| L3 | Blank
| L1 | Blank
23 | L2 | Blank
| L3 | Blank
| L1 | Blank
24 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project
Refer to electrical distribution schematic reference 27618-HM-ZZ-ZZ-DR-ES-1100 for further details

## E979002 (LB-MS)
E979002 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB LB-MS (Landlord Basement Mechanical Services)
BOARD TYPE: |  |  | 6-WAY TPN MCB
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB/16L1L2L3
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Basement LV Switchroom
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
| L1 | Basement South Electrical Riser | DB LB-MSS | 10 | arm | 2c XLPE/SWA/LSF | 63A Type C
1 | L2 | 57 Spring Gardens Basement | DB Mist | 10 | arm | 2c XLPE/SWA/LSF | 63A Type C
| L3 | Blank
| L1 | Blank
2 | L2 | Ground Floor Tenant TG02 | DB TG02-MSS | 10 | arm | 2c XLPE/SWA/LSF | 63A Type C
| L3 | 1st Floor South Electrical Riser | DB TF03-MSS | 10 | arm | 2c XLPE/SWA/LSF | 63A Type C
| L1 | 2nd Floor South Electrical Riser | DB TS04-MSS | 10 | arm | 2c XLPE/SWA/LSF | 63A Type C
3 | L2 | 2nd Floor North Electrical Riser | DB TS05-MSN | 16 | arm | 2c XLPE/SWA/LSF | 63A Type C
| L3 | 3rd Floor South Electrical Riser | DB TT06-MSS | 10 | arm | 2c XLPE/SWA/LSF | 63A Type C
| L1 | 3rd Floor North Electrical Riser | DB TT07-MSN | 16.0 | arm | 2c XLPE/SWA/LSF | 63A Type C
4 | L2 | Blank
| L3 | Blank
| L1 | Ground South Electrical Riser | DB LG-MSS | 10 | arm | 4c XLPE/SWA/LSF | 63A Type C
5 | L2
L3
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
| L1 | CSP | General Power | 4 | 4 | 3 x 1c XLPE/LSF | 20A RCBO
9 | L2 | Sorting Hall | General Power | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 16A RCBO
| L3 | DOM Office | General Power | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 16A RCBO
| L1 | Priority Services | General Power | 4 | 4 | 3 x 1c XLPE/LSF | 20A RCBO
10 | L2 | Sorting Hall | General Power | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 16A RCBO
| L3 | DOM Office | General Power | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 16A RCBO
| L1 | Priority Services | Intruder alarm panel | 4 | 4 | 3 x 1c XLPE/LSF | 20A Type B
11 | L2 | Sorting Hall | General Power | 4 | 4 | 3 x 1c XLPE/LSF | 20A RCBO
| L3 | DOM Office | Power for CCTV Equip. | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 16A Type B
| L1 | Welfare | General Power | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 32A RCBO | Ring circuit
12 | L2 | Disabled / Ladies Toilets | Hand Driers | 4 | 4 | 3 x 1c XLPE/LSF | 20A RCBO
| L3 | Disabled Toilet | Toilet Alarm | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 16A Type B
| L1 | Welfare | General Power | 2.5 | 2.5 | 3 x 1c XLPE/LSF | 16A RCBO
13 | L2 | Ladies / Gents | Hand Driers | 4 | 4 | 3 x 1c XLPE/LSF | 20A RCBO
L3
| L1 | External | Jet Wash Power | 4 | 4 | 2c XLPE/SWA/LSF | 20A RCBO
14 | L2 | Blank
| L3 | Sorting Hall | Data Cabinet Supply | 2.5 | 2.5 | 2c XLPE/SWA/LSF | 16A RCBO
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979003 (LB-GLP)
E979003 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB LB-GLP (Landlord Basement General Lighting & power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Basement South Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Basement circulation | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
1 | L2 | Bike Store | Bike charging sockets | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L3 | Gym | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L1 | Basement Toilets | Hand Drier/Alarm | 6 | 6 | 3c XLPE/LSF | 32A Type B RCBO | Radial circuit
2 | L2 | Gym | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L3 | Gym | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L1 | Basement circulation | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
3 | L2 | Gym | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L3 | Gym | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L1 | Comms Room | BS EN 60309-1 Socket | 2.5 | arm | 2c XLPE/SWA/LSF | 16A Type D RCBO | Radial circuit
4 | L2 | Blank
| L3 | 3rd Floor Circulation | General Small Power | 6 | 6 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L1 | Comms Room | BS EN 60309-1 Socket | 2.5 | arm | 2c XLPE/SWA/LSF | 16A Type D RCBO | Radial circuit
5 | L2 | 1st Floor Toilets | Hand Driers | 6 | 6 | 3c XLPE/LSF | 32A Type B RCBO | Radial circuit
| L3 | 2nd Floor Toilets | Hand Driers | 6 | 6 | 3c XLPE/LSF | 32A Type B RCBO | Radial circuit
| L1 | 3rd Floor Toilets | Hand Driers | 6 | 6 | 3c XLPE/LSF | 32A Type B RCBO | Radial circuit
6 | L2 | 1st Floor circulation | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L3 | 2nd Floor circulation | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L1 | 1st Floor Lift | Fire Shutter Supply | 4 | 4 | 3c XLPE/LSF | 20A Type B | Radial circuit
7 | L2 | 2nd Floor Lift | Fire Shutter Supply | 4 | 4 | 3c XLPE/LSF | 20A Type B | Radial circuit
| L3 | 3rd Floor Lift | Fire Shutter Supply | 4 | 4 | 3c XLPE/LSF | 20A Type B | Radial circuit
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | South Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Stair B | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Changing Rooms | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B RCBO
| L1 | Gym | Track Lighting | 1.5 | 1,5 | 3c XLPE/LSF | 10A Type B
10 | L2 | Bike Store/Corridor | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Changing Rooms | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B RCBO
| L1 | Gym | Track Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
11 | L2 | Corridor | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Changing Rooms | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B RCBO
| L1 | Gym | Track Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
12 | L2 | Corridor | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Blank
| L1 | Blank
13 | L2 | Corridor | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Blank
| L1 | Blank
14 | L2 | Blank
| L3 | Blank
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979004 (LG-GLPS)
E979004 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB LG-GLPS (Landlord Ground Floor South General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Ground Floor South Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Ground Floor Circulation | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
1 | L2 | Ground Floor Toilets | Hand Driers | 4 | 4 | 3c XLPE/LSF | 32A Type B RCBO | Radial circuit
| L3 | Ground Floor DDA Toilet | Hand Drier/Alarm | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L1 | Lounge | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
2 | L2 | Lounge | USB Socket Outlets | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L3 | Lounge Kitchenette | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO | Radial circuit
| L1 | Main Entrance | Electric Doors | 4 | 4 | 3c XLPE/LSF | 20A Type B | Radial circuit
3 | L2 | Main Entrance | DDA Steps | 4 | 4 | 3c XLPE/LSF | 20A Type B | Radial circuit
| L3 | Blank
| L1 | Lounge Kitchenette | Coffee Machine | 4 | 4 | 3c XLPE/LSF | 20A Type B | Radial circuit
4 | L2 | Lounge Kitchenette | Zip Tap | 4 | 4 | 3c XLPE/LSF | 20A Type B | Radial circuit
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Main Entrance | Powered Door | 2.5 | 2.5 | 4c XLPE/SWA/LSF | 20A Type B | Radial circuit
8 | L2
L3
Lower Pan (Lighting)
| L1 | South Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Ground Floor Corridor | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Ground Floor Stair C | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Lounge | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
10 | L2 | Ground Floor Corridor | Pendant Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | DDA Toilet & Refuse | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Lounge | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
11 | L2 | 1st Floor Toilets | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | 1st Floor Stair C | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Lounge | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
12 | L2 | 2nd Floor Toilets | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | 2nd Floor Stair C | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Lounge | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
13 | L2 | 3rd Floor Toilets | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | 3rd Floor Stair C | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Lounge | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
14 | L2
| L3 | 3rd Floor Corridor | Pendnant Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Lounge | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
15 | L2 | Blank
| L3 | Blank
| L1 | Lounge | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979005 (LG-GLPN)
E979005 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB LG-GLPN (Landlord Ground Floor North General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Ground Floor North Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Grd/1st Floor Stair D | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO
1 | L2 | 2nd Floor Toilet | Hand Driers | 6 | 6 | 3c XLPE/LSF | 32A Type B RCBO
| L3 | 3rd Floor Toilet | Hand Driers | 6 | 6 | 3c XLPE/LSF | 32A Type B RCBO
| L1 | 2nd Floor Circulation | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO
2 | L2 | 2nd Floor Circulation | Electric panel heaters | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO
| L3 | 3rd Floor Plant Stair | ASD Power Supply | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
| L1 | 3rd Floor Circulation | General Small Power | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO
3 | L2 | 3rd Floor Circulation | Electric panel heaters | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO
| L3 | 3rd Floor Cupboard | Comms Cabinet Supply | 4 | 4 | 3c XLPE/LSF | 20A Type B RCBO
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | North Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Ground Floor Stair D | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Blank
| L1 | 2nd Floor Circulation | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
10 | L2 | 3rd Floor Circulation | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Blank
| L1 | 2nd Floor Toilets | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
11 | L2 | 3rd Floor Toilets | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Blank
| L1 | Blank
12 | L2 | Blank
| L3 | Blank
| L1 | Blank
13 | L2 | Blank
| L3 | Blank
| L1 | Blank
14 | L2 | Blank
| L3 | Blank
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979006 (TG02-GLP)
E979006 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB TG02-GLPS (Tenant TG02 Ground Floor South General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Ground Floor Tenant TG02
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Office Suite 01 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
1 | L2 | Blank
| L3 | Blank
| L1 | Blank
2 | L2 | Blank
| L3 | Blank
| L1 | Blank
3 | L2 | Blank
| L3 | Blank
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | Office Suite 01 | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Office Suite 01 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 01 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 01 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
10 | L2 | Office Suite 01 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
L3
L1
11 | L2
L3
L1
12 | L2
L3
L1
13 | L2
L3
L1
14 | L2
L3
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979007 (TF03-GLPS)
E979007 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB TF03-GLPS (Tenant TF03 1st Floor South General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | 1st Floor South Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Office Suite 02 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
1 | L2 | Office Suite 02 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
| L3 | Blank
| L1 | Blank
2 | L2 | Blank
| L3 | Blank
| L1 | Blank
3 | L2 | Blank
| L3 | Blank
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | 1st Floor Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Office Suite 02 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 02 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 02 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
10 | L2 | Office Suite 02 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 02 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 02 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
11 | L2 | Office Suite 02 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Blank
| L1 | Blank
12 | L2 | Blank
| L3 | Blank
| L1 | Blank
13 | L2 | Blank
| L3 | Blank
| L1 | Blank
14 | L2 | Blank
| L3 | Blank
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979008 (TS04-GLP)
E979008 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB TS04-GLPS (Tenant TS04 2nd Floor South General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | 2nd Floor South Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Office Suite 03 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
1 | L2 | Office Suite 03 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
| L3 | Blank
| L1 | Blank
2 | L2 | Blank
| L3 | Blank
| L1 | Blank
3 | L2 | Blank
| L3 | Blank
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | 2nd Floor Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Office Suite 03 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 03 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 03 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
10 | L2 | Office Suite 03 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 03 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 03 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
11 | L2 | Blank
| L3 | Blank
| L1 | Blank
12 | L2 | Blank
| L3 | Blank
| L1 | Blank
13 | L2 | Blank
| L3 | Blank
| L1 | Blank
14 | L2 | Blank
| L3 | Blank
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979009 (TS05-GLP)
E979009 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB TS05-GLPN (Tenant TS05 2nd Floor North General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | 2nd Floor North Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Office Suite 04 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
1 | L2 | Office Suite 05 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
| L3 | Office Suite 06 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
| L1 | Blank
2 | L2 | Blank
| L3 | Blank
| L1 | Blank
3 | L2 | Blank
| L3 | Blank
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | 2nd Floor Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Office Suite 04 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 05 | Downlight Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 06 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
10 | L2 | Office Suite 04 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 05 | Downlight Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 06 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
11 | L2 | Blank
| L3 | Office Suite 05 | Downlight Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Blank
12 | L2 | Blank
| L3 | Office Suite 05 | Downlight Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Blank
13 | L2 | Blank
| L3 | Office Suite 05 | Pendant Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Blank
14 | L2 | Blank
| L3 | Office Suite 05 | Cove Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979010 (TT06-GLP)
E979010 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB TT06-GLPS (Tenant TT06 3rd Floor South General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | 3rd Floor South Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Office Suite 07 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
1 | L2 | Office Suite 07 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
| L3 | Blank
| L1 | Blank
2 | L2 | Blank
| L3 | Blank
| L1 | Blank
3 | L2 | Blank
| L3 | Blank
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | 3rd Floor Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Office Suite 07 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 07 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 07 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
10 | L2 | Office Suite 07 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 07 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Office Suite 07 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
11 | L2 | Blank
| L3 | Blank
| L1 | Blank
12 | L2 | Blank
| L3 | Blank
| L1 | Blank
13 | L2 | Blank
| L3 | Blank
| L1 | Blank
14 | L2 | Blank
| L3 | Blank
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979011 (TT07-GLP)
E979011 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB TT07-GLPN (Tenant TT07 3rd Floor North General Lighting & Power)
BOARD TYPE: |  |  | 8+8 WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 100A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | 3rd Floor North Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Office Suite 08 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
1 | L2 | Office Suite 09 | General Small Power | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B RCBO
| L3 | Blank
| L1 | Blank
2 | L2 | Blank
| L3 | Blank
| L1 | Blank
3 | L2 | Blank
| L3 | Blank
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
| L1 | Blank
5 | L2 | Blank
| L3 | Blank
| L1 | Blank
6 | L2 | Blank
| L3 | Blank
| L1 | Blank
7 | L2 | Blank
| L3 | Blank
| L1 | Blank
8 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | 3rd Floor Electrical Riser | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
9 | L2 | Office Suite 08 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 09 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Blank
10 | L2 | Office Suite 08 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 09 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Blank
11 | L2 | Office Suite 08 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Office Suite 09 | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Blank
12 | L2 | Blank
| L3 | Blank
| L1 | Blank
13 | L2 | Blank
| L3 | Blank
| L1 | Blank
14 | L2 | Blank
| L3 | Blank
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979012 (LR-GLP)
E979012 |  |  | SCHEDULE OF DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB LR-GLP (General Lighting & power)
BOARD TYPE: |  |  | 18+4-WAY TPN MCB Split Section Distribution Board
INCOMING DEVICE: |  |  | 250A switch disconnector
SUPPLY ORIGIN: |  |  | Main Switchboard MSB
PROTECTIVE DEVICE: |  |  | 250A BS 88 HRC Fuse
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Roof Plant Room
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
Upper Pan (Power)
| L1 | Roof | Basement External Condenser Unit Ref DEX/RF/07 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
1 | L2
L3
| L1 | Roof | Ground Floor External Condenser Unit Ref DEX/RF/08 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
2 | L2
L3
| L1 | Roof | 1st Floor External Condenser Unit Ref DEX/RF/09 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
3 | L2
L3
| L1 | Roof | 1st Floor External Condenser Unit Ref DEX/RF/10 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
4 | L2
L3
| L1 | Roof | 2nd Floor External Condenser Unit Ref DEX/RF/11 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
5 | L2
L3
| L1 | Roof | 2nd Floor External Condenser Unit Ref DEX/RF/12 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
6 | L2
L3
| L1 | Roof | 3rd Floor External Condenser Unit Ref DEX/RF/13 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
7 | L2
L3
| L1 | Roof | 3rd Floor External Condenser Unit Ref DEX/RF/14 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
8 | L2
L3
| L1 | Roof | 3rd Floor External Condenser Unit Ref DEX/RF/15 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
9 | L2
L3
| L1 | Roof | Basement Comms Room DX Unit Ref DEX/RF/05 | 2.5 | arm | XLPE/SWA/LSF | 20A Type D | Powertag meter to be fitted to outgoing way
10 | L2 | Roof | Basement Comms Room DX Unit Ref DEX/RF/06 | 2.5 | arm | XLPE/SWA/LSF | 20A Type D | Powertag meter to be fitted to outgoing way
| L3 | Blank
| L1 | Roof | DHW & Radiators Air Source Heat Pump Ref ASHP/RF/01 | 4 | arm | XLPE/SWA/LSF | 40A Type D | Powertag meter to be fitted to outgoing way
11 | L2
L3
| L1 | Blank
12 | L2 | Blank
| L3 | Blank
| L1 | Blank
13 | L2 | Blank
| L3 | Blank
| L1 | Blank
14 | L2 | Blank
| L3 | Blank
| L1 | Blank
15 | L2 | Blank
| L3 | Blank
| L1 | Blank
16 | L2 | Blank
| L3 | Blank
| L1 | Blank
17 | L2 | Blank
| L3 | Blank
| L1 | Blank
18 | L2 | Blank
| L3 | Blank
Lower Pan (Lighting)
| L1 | Roof Plant Room | Lighting Control Panels | 2.5 | 2.5 | 3c XLPE/LSF | 20A Type B
19 | L2 | Roof Plant Room | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L3 | Roof Plant Room | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
| L1 | Roof Plant Room | Lighting | 1.5 | 1.5 | 3c XLPE/LSF | 10A Type B
20 | L2 | Blank
| L3 | Blank
| L1 | Blank
21 | L2 | Blank
| L3 | Blank
| L1 | Blank
22 | L2 | Blank
| L3 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979013 (LB-MSS)
E970713 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | DB LB-MSS (Landlord Basement Mechanical Services)
BOARD TYPE: |  | 10 WAY SPN MCB Distribution Board
INCOMING DEVICE: |  | 125A switch disconnector
SUPPLY ORIGIN: |  | DB LB-MS/1L1
PROTECTIVE DEVICE: |  | 63A Type C MCB
SUPPLY VOLTAGE: | DB LB-MS | 230/400V
LOCATION: |  | Basement Electrical Riser South
CIRCUIT REFERENCE | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Gym | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 16A Type B | Radial Circuit
2 | Comms Room | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 16A Type B | Radial Circuit
3 | Comms Room | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 16A Type B | Radial Circuit
4 | Blank
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | DB LG-MSS
10 | DB LG-MS2
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
9 | Blank
10 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979014 (LG-MSS)
E970714 |  |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  |  | 27618
REVISION: |  |  | P01
PROJECT NAME: |  |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  |  | DB LG-MSS (Landlord Ground Floor Mechanical Services)
BOARD TYPE: |  |  | 4 WAY TPN MCB Distribution Board
INCOMING DEVICE: |  |  | 125A switch disconnector
SUPPLY ORIGIN: |  |  | DB LB-MS/5L1L2L3
PROTECTIVE DEVICE: |  |  | 63A Type C MCB
SUPPLY VOLTAGE: |  |  | 230/400V
LOCATION: |  |  | Ground South Electrical Riser
CIRCUIT REFERENCE |  | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
| L1 | Lounge | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B RCBO | Radial Circuit
1 | L2 | Blank
| L3 | Blank
| L1 | Main Entrance | Overdoor Heater | 2.5 | 2.5 | 4c XLPE/SWA/LSF | 20A Type B | Radial Circuit
2 | L2
L3
| L1 | Blank
3 | L2 | Blank
| L3 | Blank
| L1 | Blank
4 | L2 | Blank
| L3 | Blank
9 |  | DB LG-MSS
10 |  | DB LG-MS2
11 |  | Blank
12 |  | Blank
13 |  | Blank
14 |  | Blank
15 |  | Blank
16 |  | Blank
17 |  | Blank
18 |  | Blank
19 |  | Blank
20 |  | Blank
21 |  | Blank
22 |  | Blank
23 |  | Blank
24 |  | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979015 (TG02-MSS)
E970715 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | DB TG02-MSS (Tenant TG02 Ground Floor Mechanical Services)
BOARD TYPE: |  | 10 WAY SPN MCB Distribution Board
INCOMING DEVICE: |  | 125A switch disconnector
SUPPLY ORIGIN: |  | DB LB-MS/2L2
PROTECTIVE DEVICE: |  | 63A Type C MCB
SUPPLY VOLTAGE: |  | 230/400V
LOCATION: |  | Ground Floor TG02
CIRCUIT REFERENCE | DB LG-GLPN | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Office Suite 01 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
2 | Office Suite 01 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
3 | Blank
4 | Blank
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | Blank
10 | Blank
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
9 | Blank
10 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979016 (TF03-MSS)
E970716 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | DB TF03-MSS (Tenant TF03 1st Floor Mechanical Services)
BOARD TYPE: |  | 10 WAY SPN MCB Distribution Board
INCOMING DEVICE: |  | 125A switch disconnector
SUPPLY ORIGIN: |  | DB LB-MS/2L3
PROTECTIVE DEVICE: |  | 63A Type C MCB
SUPPLY VOLTAGE: |  | 230/400V
LOCATION: |  | 1st Floor South Electrical Riser
CIRCUIT REFERENCE | DB LG-GLPN | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Office Suite 02 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
2 | Office Suite 02 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
3 | Blank
4 | Blank
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | Blank
10 | Blank
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
9 | Blank
10 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979017 (TS04-MSS)
E970717 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | DB TS04-MSS (Tenant TS04 2nd Floor South Mechanical Services)
BOARD TYPE: |  | 10 WAY SPN MCB Distribution Board
INCOMING DEVICE: |  | 125A switch disconnector
SUPPLY ORIGIN: |  | DB LB-MS/3L1
PROTECTIVE DEVICE: |  | 63A Type C MCB
SUPPLY VOLTAGE: |  | 230/400V
LOCATION: |  | 2nd Floor South Electrical Riser
CIRCUIT REFERENCE | DB LG-GLPN | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Office Suite 03 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
2 | Office Suite 03 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
3 | Office Suite 03 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
4 | Blank
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | Blank
10 | Blank
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
9 | Blank
10 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979018 (TS05-MSN)
E970718 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | DB TS05-MSN (Tenant TS05 2nd Floor North Mechanical Services)
BOARD TYPE: |  | 10 WAY SPN MCB Distribution Board
INCOMING DEVICE: |  | 125A switch disconnector
SUPPLY ORIGIN: |  | DB LB-MS/3L2
PROTECTIVE DEVICE: |  | 63A Type C MCB
SUPPLY VOLTAGE: |  | 230/400V
LOCATION: |  | 2nd Floor North Electrical Riser
CIRCUIT REFERENCE | DB LG-GLPN | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Office Suite 04 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial circuit
2 | Office Suite 05 | High Level Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial circuit
3 | Office Suite 05 | Low Level Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial circuit
4 | Office Suite 06 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial circuit
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | Blank
10 | Blank
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
9 | Blank
10 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979019 (TT06-MSS)
E970719 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | DB TT06-MSS (Tenant TT06 3rd Floor South Mechanical Services)
BOARD TYPE: |  | 10 WAY SPN MCB Distribution Board
INCOMING DEVICE: |  | 125A switch disconnector
SUPPLY ORIGIN: |  | DB LB-MS/3L3
PROTECTIVE DEVICE: |  | 63A Type C MCB
SUPPLY VOLTAGE: |  | 230/400V
LOCATION: |  | 3rd Floor South Electrical Riser
CIRCUIT REFERENCE | DB LG-GLPN | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Office Suite 07 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
2 | Office Suite 07 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
3 | Office Suite 07 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
4 | Blank
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | Blank
10 | Blank
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
9 | Blank
10 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979020 (TT07-MSN)
E979020 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | DB TT07-MS2 (Tenant TT07 3rd Floor North Mechanical Services)
BOARD TYPE: |  | 8 WAY SPN MCB Distribution Board
INCOMING DEVICE: |  | 125A switch disconnector
SUPPLY ORIGIN: |  | DB LB-MS/4L1
PROTECTIVE DEVICE: |  | 63A Type C MCB
SUPPLY VOLTAGE: |  | 230/400V
LOCATION: |  | 3rd Floor North Electrical Riser
CIRCUIT REFERENCE | DB LG-GLPN | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Office Suite 08 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
2 | Office Suite 09 | Fan Coil Units | 2.5 | arm | 2c XLPE/SWA/LSF | 20A Type B | Radial Circuit
3 | Blank
4 | Blank
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | Blank
10 | Blank
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
9 | Blank
10 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## E979013
E979013 |  | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: |  | 27618
REVISION: |  | P01
PROJECT NAME: |  | 38-42 MOSLEY STREET GRADE 2* LISTED BUILDING CAT A REFURBISHMENT
BOARD REF: |  | TBC
BOARD TYPE: |  | TBC-WAY SPN MCB
INCOMING DEVICE: |  | TBC
SUPPLY ORIGIN: |  | TBC
PROTECTIVE DEVICE: |  | TBC
SUPPLY VOLTAGE: |  | 230V
LOCATION: |  | TBC
CIRCUIT REFERENCE | LOCATION | ITEM | CABLE SIZE (mm²) | CPC (mm2) | CABLE TYPE | CPD RATING & TYPE | COMMENTS
1 | Blank
2 | Blank
3 | Blank
4 | Blank
5 | Blank
6 | Blank
7 | Blank
8 | Blank
9 | Blank
10 | Blank
11 | Blank
12 | Blank
13 | Blank
14 | Blank
15 | Blank
16 | Blank
17 | Blank
18 | Blank
19 | Blank
20 | Blank
21 | Blank
22 | Blank
23 | Blank
24 | Blank
To be read in conjunction Section E31 and E34 and the Scope of Services and Design Parameters Sections of the Electrical Services Specification
DELETE PRIOR TO ISSUE - Notes to Author. Edit Schedule in accordance with specific requirements of Project

## Notes
NOTES | SCHEDULE OF LANDLORDS DISTRIBUTION BOARDS
HM PROJECT: | TBC
REVISION: | 00
PROJECT NAME: | TBC
01 | Distribution Boards shall be selected in accordance with the specifc requirements of the Services Description and Section E31
02 | Protective and Switching Devices shall be selected in accordance with the specifc requirements of the Services Description and Section E34
03 | Cables shall be selected in accordance with the requirements of the Services Description and Section E08 of the Project Specification
04 | Cables shall be sourced directly from the recognised cable manufactures listed within Schedule E970004
05 | Cables shall be installed on and in containment systems in accordance with the Services Description and section E10 of the Project Specification
DELETE PRIOR TO ISSUE - All notes are provided for guidance and shall be checked and amended to ensure they fully reflect the project specific requirements