## Sheet1
EVIDENCE OF MECHANICAL VENTILATION FLOW RATE TESTING - TESTING OF FIXED FANS
AIR FLOW MEASUREMENT (FIXED SYSTEM 1 FANS ONLY)
Customer |  |  | Miller Homes
Dwelling Address |  |  | Plot 060 - 13 Rollins Close - M230JZ
Test Date |  |  | 2025-06-09
TEST EQUIPMENT
Air Flow Measurement Equipment Used |  |  | TSI AIRFLOW LCA 301
(Please state model and type)
Date of UKAS Calibration |  |  | 26/04/24 | Certificate No. |  | AFL72850901
Model No. |  |  | 255919
Test Method Used |  |  | Tick | Please Refer to NHBC Guidance Note for Furter Information on Methods
Method 1 - Unconditional Method |  |  | YES | Complete boxes (a), (b), (c), (d), (g) and (h)
Method 2 - Conditional Method |  |  |  | Complete boxes (a), (b), (c), (d), (e), (f), (g) and (h)
Method 3 - Minimum Benchmark Method |  |  |  | Complete boxes (a), (b), (c), (d), (g) and (h)
(15 l/s = 12 (l/s), (30 l/s =24 l/s) or (60 l/s = 35 l/s)
AIR FLOW MEASUREMENTS
(a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i)
Fan Reference | Manufacturer | Model | Measured extract rate (l/s) | Fan correction factor | Corrected extract rate (l/s) | Design extract rate (l/s) | Pass/Fail | Reason for Failure
KITCHEN | Vent-Axia | 498095 | 15.4 | N/A | N/A | 15 | PASS
W.C. | Vent-Axia | 498095 | 15.2 | N/A | N/A | 15 | PASS
BATHROOM | Vent-Axia | 498095 | 15.6 | N/A | N/A | 15 | PASS
ENSUITE | Vent-Axia | 498095 | 15,9 | N/A | N/A | 15 | PASS
UTILITY | Vent-Axia | 498095 | 15.2 | N/A | N/A | 15 | PASS
TEST ENGINEER'S DETAILS
Name | LUKE STACEY
Company | STACEY ELECTRICAL SERVICES
Address | 119 ST. MARY'S STREET, LATCHFORD, WARRIGTON, WA41EW
Telephone | 07887842845
Email | luke@staceyelectrical.com
For further advice please contact an NHBC surveyor on 0844 633 1000 and ask for 'Building Control'.