Unit 3, School Street Trading Estate, School Street, Stockport, SK7 4RA

Kitchen Extraction and supply air design

1 Chorlton, Place, Chorlton, Manchester, M21 9AQ

Extraction System

Extract based on a canopy size of 5800 x 1500 wall type canopy

- Volume of canopy requires a volume of 1.58 m3/sec with a total air volume

- Duct size off each canopy would be 500mm diameter, fabricated duct

- Extract spigots on canopy 1 x 500

- Fan selection 1 off MUB 042 500 EV MultiBox Fan

- 1 of 500 MUB SIL Silencer

- System to be terminated by a flat roof cowl.

- DBA of Fan 64 DBA

- Odour control MFU 1200 MODEL A1 (C)

Supply air System

Supply air system based on 80% of the extraction rate

- Flow rate for system 1.26 m3/sec

- main header duct size of 300mm diameter fabricated duct

- Supply air grill spigot sizes 200mm to each grill

- Ceiling grills 4 off 595 mm x 595 mm 4-way diffuser c/w dampers

- Fan selection 1 off AW 450E4 Plate Mounted Fan

- 1 off 450mm 1D No Pod Silencers

- Terminated Via RAW 400/450 Roof Unit

- DBA of Fan 48 DBA