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Unit 3, School Street Trading Estate, School Street, Stockport, SK7 4RA


Kitchen Extraction and supply air design 
1 Chorlton, Place, Chorlton, Manchester, M21 9AQ

Extraction System 

 Extract based on a canopy size of 5800 x 1500 wall type canopy 

· Volume of canopy requires a volume of 1.58 m3/sec with a total air volume 
· Duct size off each canopy would be 500mm diameter, fabricated duct
· Extract spigots on canopy 1 x 500
· Fan selection 1 off MUB 042 500 EV MultiBox Fan      
· 1 of 500 MUB SIL Silencer 
· System to be terminated by a flat roof cowl. 
· DBA of Fan 64 DBA
· Odour control MFU 1200 MODEL A1 (C)

Supply air System 

Supply air system based on 80% of the extraction rate

· Flow rate for system 1.26 m3/sec
· main header duct size of 300mm diameter fabricated duct
· Supply air grill spigot sizes 200mm to each grill 
· Ceiling grills 4 off 595 mm x 595 mm 4-way diffuser c/w dampers 
· Fan selection 1 off AW 450E4 Plate Mounted Fan   
· [bookmark: _Hlk190355226]1 off 450mm 1D No Pod Silencers  
· [bookmark: _Hlk190355261]Terminated Via RAW 400/450 Roof Unit  
· DBA of Fan 48 DBA
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