	Proprietary Treatment Systems

	Maintenance Schedule
	Required Action
	Typical Frequency

	Routine Maintenance
	Remove litter and debris and inspect for sediment, oil and grease accumulation
	Six monthly

	
	Change the filter media
	As recommended by manufacturer

	
	Remove sediment, oil, grease and floatables
	As necessary – indicated by system
inspections or immediately following significant spill

	Remedial Actions
	Replace malfunctioning parts or structures
	As required

	Monitoring
	Inspect for evidence of poor operation
	Six monthly

	
	Inspect filter media and establish appropriate replacement frequencies
	Six monthly

	
	Inspect sediment accumulation rates and establish appropriate removal frequencies
	Monthly during first half years of operation, then every six months




	Bioretention Systems

	Maintenance Schedule
	Required Action
	Typical Frequency

	Regular Inspections
	Inspect infiltration surfaces for silting and ponding, record de-watering time of the facility and assess standing water levels in underdrain
(if appropriate) to determine if maintenance is necessary
	Quarterly

	
	Check operation of underdrains by inspection of flows after rain
	Annually

	
	Assess plants for disease infection, poor growth, invasive species etc and replace as necessary
	Quarterly

	
	Inspect inlets and outlets for blockage
	Quarterly

	Regular Maintenance
	Remove litter and surface debris and weeds
	Quarterly (or more frequently for tidiness or aesthetic reasons)

	
	Replace any plants, to maintain planting density
	As required

	
	Remove sediment, litter and debris build-up from around inlets or from forebays
	Quarterly to biannually

	Occasional Maintenance
	Infill any holes or scour in the filter medium, improve erosion protection if required
	As required

	
	Repair minor accumulation of silt by raking away surface mulch, scarifying surface of medium and replacing mulch
	As required

	Remedial Actions
	Remove and replace filter medium and vegetation above
	As required but likely to be > 20 years



