PROLOCO

The Wilco Test Ltd t/a Proloco

Fume Extraction - Cleaning and Maintenance Regime

Prepared in support of planning condition discharge (Condition 19 - Ventilation / Extract)

| Premises | Proloco, Unit 2, One Port Street, 74 Great Ancoats Street, Manchester M4 5GU |
| --- | --- |
| Operator | The Wilco Test Ltd t/a Proloco |
| Scope | Cleaning and maintenance regime for kitchen fume extraction equipment |
| Date | July 2026 |
| Version | 1.0 |

Note on scope: This statement addresses the third information item requested under Condition 19 - the proposed cleaning and maintenance regime for the fume extraction equipment. The Full Odour Impact Assessment and the internal floorplans showing equipment location and ducting route are being provided separately by the operator's specialist consultant and by PHAUS respectively.

# 1. Extraction system overview

The kitchen extraction system comprises a canopy and filtration arrangement serving the pizza oven and cooking line, ducted to [discharge point - roof level / external wall, per PHAUS drawings]. The system incorporates grease filtration and odour control appropriate to the cooking operation. Full equipment specification has already been provided to the Council under separate cover; this document addresses the ongoing cleaning and maintenance of that equipment.

# 2. Cleaning regime

The operator will maintain the extraction system to the standard of TR19 Grease (the Building Engineering Services Association specification for the cleanliness of kitchen extract systems), which is the recognised industry benchmark and is also required by the operator's insurers. The regime is as follows:

| Element | Task | Frequency | Responsibility |
| --- | --- | --- | --- |
| Grease filters | Removed, degreased and cleaned (or replaced) | Daily / after each service as required | Kitchen team |
| Canopy internal surfaces | Degreased and wiped down | Daily | Kitchen team |
| Ductwork (full length) | Deep clean by specialist contractor to TR19 Grease, with pre/post clean report and access-panel verification | Per TR19 Grease, by usage category (see note below) | Specialist contractor |
| Fan and extract unit | Cleaned and inspected | With each ductwork deep clean | Specialist contractor |
| Odour control media | Inspected and replaced per manufacturer schedule | Per manufacturer recommendation | Specialist contractor |

The operator commits to maintaining the system to the TR19 Grease standard and to whatever deep-clean frequency that standard requires for the premises' usage category. Under TR19 Grease, deep-clean frequency is determined by daily cooking hours: heavy use (12+ hours per day) every six months; medium use (6 to 12 hours per day) annually; light use (2 to 6 hours per day) annually. The applicable category will be confirmed with the appointed specialist contractor once trading hours are established. The cleaning contractor will be appointed prior to opening.

# 3. Maintenance and record keeping

- A planned preventative maintenance (PPM) schedule will be held for the extraction and abatement equipment, following manufacturer recommendations.

- Post-clean certificates and TR19 Grease reports (including before/after photographic evidence and access panel records) will be retained on site and made available to the Council's Environmental Protection team and to insurers on request.

- Any fault affecting the performance of the extraction or odour abatement system will be reported and rectified promptly; the system will not be operated in a degraded state that could give rise to odour or emissions nuisance.

- Filter changes and in-house cleaning tasks will be logged as part of the kitchen's daily and weekly compliance checklists.

# 4. Responsibility

Overall responsibility for the extraction cleaning and maintenance regime sits with the Head of Kitchen, with the Creative Director holding ultimate accountability for kitchen compliance. Records are subject to periodic review by management.